## README
Item | Description
Purpose | Machine-readable correspondence tables between the TBIM (Topologic JSON), IFC, Honeybee (HB) and EnergyPlus (E+) used by the BIM-to-BEM workflow, plus the values actually present in each model. They extend Tables 7, 8 and 9 of the Appendix of the paper.
Workflow analysed | scripts/01_bim_to_bem.py, src/digitmanpy/Operation.py (classes Utils, HB, Eppy, TBIM). The tuning (scripts/02_bem_calibration.py) edits the IDF directly.
Value sources | TBIM: data/<building>/<building>_tbim_topologic.json (Cell / Face / Aperture dictionaries). IFC: *_tbim_ifc_design_transfer_view.ifc (spaces, element types, glazing psets) and *_tbim_ifc_reference_view.ifc (material properties). E+: models/*_bem_baseline.idf (baseline = direct output of the workflow) and models/*_bem_calibrated.idf (after manual calibration). Schedules: data/schedules/*.json.
Author decisions (2026-10-16) | Report the CALIBRATED model and replace Appendix values with model values, EXCEPT ventilation/infiltration (EN 16798 values already in the paper) and temperature setpoints (values cited in the paper: 20 / 15 °C heating, 26 °C cooling), both kept in Ref_Assumptions. Table 8 = every outer-envelope construction; Table 7 indexed by EnergyPlus zone; Table 9 reports the 23 B09 curtain-wall panels with their BIM glazing (VT 0.58).
Sheet: Ref_Assumptions | Reference ventilation/infiltration inputs (yellow, editable) used by T7, plus AHU-capacity checks.
Sheet: T7_Zones / T7_Grouped | Proposed Appendix Table 7: one row per E+ zone (calibrated IDF) and a condensed version grouping identical zones (for the manuscript).
Sheet: T8_Envelope | Proposed Appendix Table 8: every outer-envelope construction with layers and computed U (live formulas).
Sheet: T9_Glazing | Proposed Appendix Table 9: glazing constructions with U/SHGC/VT, BIM glass/frame data and areas.
Sheet: Map_Spaces | Space / zone properties (Appendix Table 7). One row per property.
Sheet: Map_Envelope | Opaque constructions, materials, surfaces and boundary conditions (Appendix Table 8).
Sheet: Map_Apertures | Windows, doors, curtain walls, blinds (Appendix Table 9).
Sheet: Map_Model | Zoning, geometry, shading, infiltration, HVAC, schedules and simulation settings (not in the Appendix today; candidate Table 10).
Sheet: Val_SpaceTypes | Actual TBIM values per occupancy type and building (what Table 7 'Assigned value' should report).
Sheet: Val_Zones | Actual E+ values per thermal zone, baseline vs calibrated IDF.
Sheet: Val_Constructions / Val_Layers | Actual opaque constructions and their layers as written in the IDF; R and U are live formulas.
Sheet: Val_Glazing | Glazing constructions in the IDF and their IFC sources.
Sheet: Val_Schedules | Schedule rulesets (JSON) → Schedule:Compact objects and where they are used.
Sheet: Issues_Questions | Discrepancies between the manuscript and the code/models, with questions for the authors.
Column 'In IDF?' | Yes = value is written to an E+ field; Partial = written with a fixed/default value or only in some cases; No = read or stored but not used by the BEM.
Naming | Topologic keys keep the original spelling used in the models (e.g. 'Trasmittance', 'Heigth', 'Costant') so they can be used as join keys.
IFC psets | Custom TBIM properties are exported by Revit in a free-text pset named 'Altro' (Building 09, Italian UI) or 'Other' (Building 10).
Units | TBIM geometry is in cm; HB/E+ in m (÷100). Ventilation rates are divided by 1000 (L/s → m3/s). See column 'Conversion'.
Colour code | Blue text = editable input/assumption (e.g. surface resistances). Black = data or formula. Green fill / yellow / orange in 'In IDF?' = Yes / Partial / No. Issues are coloured by severity.
Generated | 2026-10-16 from the files listed above (no values typed by hand except where a row says 'notebook constant' or 'HB default').

## Ref_Assumptions
Key | Parameter | Value | Unit | Source / note
OA_per_person | Outdoor air per person (occupied, ventilated zones) | 10 | L/s·person | Value reported in the paper (Methods, EN 16798-1 Cat. II); author decision 2026-10-16. Repository IDF: 7 L/s·p.
OA_per_area | Outdoor air per floor area (building emissions) | 0.6 | L/s·m² | Value reported in the paper (Methods); author decision 2026-10-16. Repository IDF: TBIM air-change rate written as L/s·m².
OA_unoccupied | Outdoor air when unoccupied / night | 0 | L/s | Methods: night-time/unoccupied lower limit = 0 (infiltration only).
Infiltration_ACH | Infiltration (envelope) | 0.3 | h⁻¹ | Methods: 0.3 ACH. Repository IDF: 0.0001 m³/s per m² exterior surface ('TightBuilding').
AHU_cap_B09 | AHU maximum airflow – Building 09 | 7200 | m³/h | Methods.
AHU_cap_B10 | AHU maximum airflow – Building 10 | 11000 | m³/h | Methods.
Heating_SP_occupied | Heating setpoint – occupied | 20 | °C | Paper Table 7 (Space Temperature Winter Max, occupied heating setpoint); author decision 2026-10-16. Calibrated IDF: B09 18 °C, B10 22 °C.
Heating_SP_setback | Heating setpoint – night / weekend setback | 15 | °C | Paper Table 7 (Space Temperature Winter Min). Calibrated IDF: B09 15 °C, B10 18 °C.
Cooling_SP_occupied | Cooling setpoint – occupied | 26 | °C | Paper Table 7 (Space Temperature Summer Max). Calibrated IDF: B09 20 °C, B10 22 °C.
Check | Sum of design outdoor airflow – B09 |  | m³/h | Compare with AHU_cap_B09 (C6).
Check | Sum of design outdoor airflow – B10 |  | m³/h | Compare with AHU_cap_B10 (C7).
Check | Design airflow / AHU capacity – B09 |  | – | > 1 means the AHU cap limits the outdoor air.
Check | Design airflow / AHU capacity – B10 |  | – | > 1 means the AHU cap limits the outdoor air.

## T7_Zones
Building | E+ zone | Zone use (inferred from E+ loads) | Floor area (m²) | Occupancy density (person/m²) | Design occupants (persons) | Occupancy schedule | Lighting power density (W/m²) | Lighting schedule | Equipment power density (W/m²) | Equipment schedule | Heating setpoint occupied (°C) – paper | Heating setback (°C) – paper | Cooling setpoint occupied (°C) – paper | RH max – dehumidification (%) | RH min – humidification (%) | HVAC availability (heating / cooling / ventilation) | Mechanically ventilated | OA per person (L/s·p) – reported | OA per area (L/s·m²) – reported | Design outdoor airflow (m³/h) | Infiltration (h⁻¹) – reported | OA per person in repository IDF (L/s·p) | TBIM air-change rate written to IDF (h⁻¹) | Heating SP in calibrated IDF (occupied / otherwise, °C) | Cooling SP in calibrated IDF (°C)
B09 | debugZone0 | Unconditioned (stairs, shafts, storage, parking) – cell not clustered | 83.06 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | debugZone1 | Unconditioned (stairs, shafts, storage, parking) – cell not clustered | 83.06 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | debugZone10 | Research laboratory – cell not clustered | 37.39 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7691 | 18 / 15 | 20
B09 | debugZone11 | Conditioned service / circulation – cell not clustered | 6.46 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | debugZone2 | Unconditioned (stairs, shafts, storage, parking) – cell not clustered | 73.89 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | debugZone3 | Unconditioned (stairs, shafts, storage, parking) – cell not clustered | 31.04 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | debugZone4 | Research laboratory – cell not clustered | 81.83 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.663 | 18 / 15 | 20
B09 | debugZone5 | Research laboratory – cell not clustered | 82.54 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.4836 | 18 / 15 | 20
B09 | debugZone6 | Research laboratory – cell not clustered | 61 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.86 | 18 / 15 | 20
B09 | debugZone7 | Research laboratory – cell not clustered | 43.26 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8059 | 18 / 15 | 20
B09 | debugZone8 | Research laboratory – cell not clustered | 46.56 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7792 | 18 / 15 | 20
B09 | debugZone9 | Research laboratory – cell not clustered | 47.26 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7518 | 18 / 15 | 20
B09 | zone00 | Unconditioned (stairs, shafts, storage, parking) | 1381.74 | 0 |  | OccSch_Unoccupied | 0 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  |  | 100 | 0 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone01 | Unconditioned (stairs, shafts, storage, parking) | 33.16 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone02 | Conditioned service / circulation | 136.45 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 8 | 18 / 15 | 20
B09 | zone03 | Unconditioned (stairs, shafts, storage, parking) | 36.74 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 1 | 18 / 15 | 20
B09 | zone04 | Unconditioned (stairs, shafts, storage, parking) | 1130.23 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 1 | 18 / 15 | 20
B09 | zone05 | Conditioned service / circulation | 38.15 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone06 | Conditioned service / circulation | 0 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone07 | Unconditioned (stairs, shafts, storage, parking) | 504.16 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 2 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone08 | Conditioned service / circulation | 5.2 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 2 | AlwaysOff |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone09 | Lecture hall / study room | 61.15 | 0.6 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.7384 | 18 / 15 | 20
B09 | zone10 | Unconditioned (stairs, shafts, storage, parking) | 561.96 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 1 | 18 / 15 | 20
B09 | zone11 | Office | 58.92 | 0.12 |  | OccSch_Unoccupied | 7 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 0.68599 | 18 / 15 | 20
B09 | zone12-0 | Conditioned service / circulation | 38.15 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone12-1 | Unconditioned (stairs, shafts, storage, parking) | 6.89 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone12-2 | Conditioned service / circulation | 20.86 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone13 | Unconditioned (stairs, shafts, storage, parking) | 70.4 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone14 | Unconditioned (stairs, shafts, storage, parking) | 651.44 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone15 | Lecture hall / study room | 109.8 | 0.6 |  | OccSch_B0.1 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.2642 | 18 / 15 | 20
B09 | zone16 | Research laboratory | 18.92 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8634 | 18 / 15 | 20
B09 | zone17 | Research laboratory | 59.15 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7926 | 18 / 15 | 20
B09 | zone18 | Research laboratory | 121.81 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7618 | 18 / 15 | 20
B09 | zone19 | Research laboratory | 39.96 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.6851 | 18 / 15 | 20
B09 | zone20 | Research laboratory | 22.76 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.479 | 18 / 15 | 20
B09 | zone21 | Lecture hall / study room | 181.84 | 0.6 |  | OccSch_B2.3 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 0.33794 | 18 / 15 | 20
B09 | zone22 | Lecture hall / study room | 184.06 | 0.6 |  | OccSch_B2.4 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.3067 | 18 / 15 | 20
B09 | zone23 | Lecture hall / study room | 183.32 | 0.6 |  | OccSch_B2.6 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.4077 | 18 / 15 | 20
B09 | zone24 | Lecture hall / study room | 182.71 | 0.6 |  | OccSch_B2.5 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.2903 | 18 / 15 | 20
B09 | zone25 | Lecture hall / study room | 109.33 | 0.6 |  | OccSch_B2.2 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.3662 | 18 / 15 | 20
B09 | zone26 | Lecture hall / study room | 183.48 | 0.6 |  | OccSch_B0.1 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.2743 | 18 / 15 | 20
B09 | zone27 | Lecture hall / study room | 183.32 | 0.6 |  | OccSch_B0.7 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.8035 | 18 / 15 | 20
B09 | zone28 | Lecture hall / study room | 105.5 | 0.6 |  | OccSch_B0.6 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.481 | 18 / 15 | 20
B09 | zone29 | Conditioned service / circulation | 5.07 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 18 / 15 | 20
B09 | zone30 | Lecture hall / study room | 51.28 | 0.6 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 2.1208 | 18 / 15 | 20
B09 | zone31 | Lecture hall / study room | 184.06 | 0.6 |  | OccSch_B0.5 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.6741 | 18 / 15 | 20
B09 | zone32 | Lecture hall / study room | 326.19 | 0.6 |  | OccSch_B1.3 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 2.9384 | 18 / 15 | 20
B09 | zone33 | Lecture hall / study room | 181.84 | 0.6 |  | OccSch_B0.4 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.5058 | 18 / 15 | 20
B09 | zone34 | Lecture hall / study room | 109.33 | 0.6 |  | OccSch_B0.3 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.3662 | 18 / 15 | 20
B09 | zone35 | Lecture hall / study room | 73.68 | 0.6 |  | OccSch_B0.2 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.3402 | 18 / 15 | 20
B09 | zone36 | Research laboratory | 123.29 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8018 | 18 / 15 | 20
B09 | zone37 | Research laboratory | 33.35 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8329 | 18 / 15 | 20
B09 | zone38 | Research laboratory | 65.35 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7161 | 18 / 15 | 20
B09 | zone39 | Research laboratory | 218.41 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7669 | 18 / 15 | 20
B09 | zone40 | Research laboratory | 32.02 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.9073 | 18 / 15 | 20
B09 | zone41 | Research laboratory | 64.03 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7542 | 18 / 15 | 20
B09 | zone42 | Research laboratory | 161.34 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8912 | 18 / 15 | 20
B09 | zone43 | Research laboratory | 59.89 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7769 | 18 / 15 | 20
B09 | zone44 | Research laboratory | 51.46 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.6995 | 18 / 15 | 20
B09 | zone45 | Lecture hall / study room | 183.32 | 0.6 |  | OccSch_B1.5 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.6731 | 18 / 15 | 20
B09 | zone46 | Lecture hall / study room | 182.71 | 0.6 |  | OccSch_B1.4 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.2903 | 18 / 15 | 20
B09 | zone47 | Lecture hall / study room | 109.33 | 0.6 |  | OccSch_B1.2 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.049 | 18 / 15 | 20
B09 | zone48 | Lecture hall / study room | 183.48 | 0.6 |  | OccSch_B1.1 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 5.5209 | 18 / 15 | 20
B09 | zone49 | Research laboratory | 53.66 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8737 | 18 / 15 | 20
B09 | zone50 | Research laboratory | 63.84 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.7667 | 18 / 15 | 20
B10 | zone00 | Conditioned service / circulation | 12.82 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 100 | 0 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 8 | 22 / 18 | 22
B10 | zone01 | Unconditioned (stairs, shafts, storage, parking) | 26.32 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 1 | 22 / 18 | 22
B10 | zone02 | Unconditioned (stairs, shafts, storage, parking) | 124.8 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone03 | Unconditioned (stairs, shafts, storage, parking) | 5.9 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone04 | Unconditioned (stairs, shafts, storage, parking) | 74.92 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone05 | Conditioned service / circulation | 38.03 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 1 | 22 / 18 | 22
B10 | zone06 | Unconditioned (stairs, shafts, storage, parking) | 8.58 | 0 |  | OccSch_A0.1/A0.2 | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 100 | 0 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone07 | Unconditioned (stairs, shafts, storage, parking) | 64.2 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone08 | Conditioned service / circulation | 537.39 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 1 | 22 / 18 | 22
B10 | zone09 | Conditioned service / circulation | 66.07 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | EqpSch_Unoccupied |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 8 | 22 / 18 | 22
B10 | zone10 | Unconditioned (stairs, shafts, storage, parking) | 20.66 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 1 | 22 / 18 | 22
B10 | zone11 | Unconditioned (stairs, shafts, storage, parking) | 287.55 | 0 |  | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  |  | 70 | 40 | Off (AlwaysOff) | No |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone12 | Snack bar | 282.3 | 0.8 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | EqpSch_Unoccupied |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 4.8113 | 22 / 18 | 22
B10 | zone13 | Conditioned service / circulation | 10.17 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone14 | Research laboratory | 65.63 | 0.3 |  | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.8315 | 22 / 18 | 22
B10 | zone15 | Lecture hall / study room | 321.56 | 0.6 |  | OccSch_A1.2 | 6 | LghSch_A1.2 | 10 | EqpSch_A1.2 |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 3.3027 | 22 / 18 | 22
B10 | zone16 | Lecture hall / study room | 217.82 | 0.6 |  | OccSch_A1.1 | 6 | LghSch_A1.1 | 10 | EqpSch_A1.1 |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.4429 | 22 / 18 | 22
B10 | zone17 | Conditioned service / circulation | 9.22 | 0 |  | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 0 | 0 | 22 / 18 | 22
B10 | zone18 | Lecture hall / study room | 394.18 | 0.6 |  | OccSch_A1.3 | 6 | LghSch_A1.3 | 10 | EqpSch_A1.3 |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 2.9711 | 22 / 18 | 22
B10 | zone19 | Lecture hall / study room | 539.86 | 0.6 |  | OccSch_A0.1/A0.2 | 6 | LghSch_A0.1/A0.2 | 10 | EqpSch_A0.1/A0.2 |  |  |  | 70 | 40 | Always on (calibrated AHU schedules = 1) | Yes |  |  |  |  | 7 | 1.5648 | 22 / 18 | 22
Note on A1: Proposed Appendix Table 7, indexed by EnergyPlus zone (author decision). Loads, schedules, setpoints and humidity limits from DigitMan_Model_POLIMI-Edificio{09,10}_EnergyPlusIDF_Calibrated.idf. Ventilation and infiltration columns S, T, V are the EN 16798 / Methods reference values (Ref_Assumptions); columns W–X keep the repository IDF values for traceability.
Note on C1: Inferred from People density and HVAC availability in the IDF (0.6 → lecture hall, 0.3 → lab, 0.12 → office, 0.8 → snack bar).
Note on D1: Sum of the areas of the zone's Floor surfaces in the IDF geometry.
Note on L1: Setpoints cited in the paper (author decision), linked to Ref_Assumptions C8:C10; '–' for unconditioned zones. Calibrated-IDF values in columns Y–Z.
Note on U1: Formula: (occupants × OA per person + area × OA per area) × 3.6, ventilated zones only.

## T7_Grouped
Building | Zone use | N zones | E+ zones | Floor area (m²) | Design occupants | Occupancy density (person/m²) | Occupancy schedule | LPD (W/m²) | Lighting schedule | EPD (W/m²) | Equipment schedule | Heating SP occupied / setback (°C) | Cooling SP (°C) | RH max / min (%) | Mech. ventilated | OA per person (L/s·p) | OA per area (L/s·m²) | Design OA (m³/h) | Infiltration (h⁻¹)
B09 | Unconditioned (stairs, shafts, storage, parking) – cell not clustered | 4 | debugZone0, debugZone1, debugZone2, debugZone3 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | No
B09 | Research laboratory – cell not clustered | 7 | debugZone10, debugZone4, debugZone5, debugZone6, debugZone7, debugZone8, debugZone9 |  |  | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Conditioned service / circulation – cell not clustered | 1 | debugZone11 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Unconditioned (stairs, shafts, storage, parking) | 1 | zone00 |  |  | 0 | OccSch_Unoccupied | 0 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  | 100 / 0 | No
B09 | Unconditioned (stairs, shafts, storage, parking) | 1 | zone01 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | No
B09 | Conditioned service / circulation | 5 | zone02, zone05, zone12-0, zone12-2, zone29 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Unconditioned (stairs, shafts, storage, parking) | 6 | zone03, zone04, zone10, zone12-1, zone13, zone14 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  | 70 / 40 | No
B09 | Conditioned service / circulation | 1 | zone06 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  | 70 / 40 | Yes
B09 | Unconditioned (stairs, shafts, storage, parking) | 1 | zone07 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 2 | AlwaysOff |  |  | 70 / 40 | No
B09 | Conditioned service / circulation | 1 | zone08 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 2 | AlwaysOff |  |  | 70 / 40 | Yes
B09 | Lecture hall / study room | 2 | zone09, zone30 |  |  | 0.6 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Office | 1 | zone11 |  |  | 0.12 | OccSch_Unoccupied | 7 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Lecture hall / study room | 18 | zone15, zone21, zone22, zone23, zone24, zone25, zone26, zone27, zone28, zone31, zone32, zone33, zone34, zone35, zone45, zone46, zone47, zone48 |  |  | 0.6 | OccSch_<room> (lecture timetable) | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B09 | Research laboratory | 16 | zone16, zone17, zone18, zone19, zone20, zone36, zone37, zone38, zone39, zone40, zone41, zone42, zone43, zone44, zone49, zone50 |  |  | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | Yes
B10 | Conditioned service / circulation | 2 | zone00, zone17 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 100 / 0 | Yes
B10 | Unconditioned (stairs, shafts, storage, parking) | 2 | zone01, zone03 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 70 / 40 | No
B10 | Unconditioned (stairs, shafts, storage, parking) | 4 | zone02, zone07, zone10, zone11 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  | 70 / 40 | No
B10 | Unconditioned (stairs, shafts, storage, parking) | 1 | zone04 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 2 | EqpSch_Costant |  |  | 70 / 40 | No
B10 | Conditioned service / circulation | 1 | zone05 |  |  | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | AlwaysOff |  |  | 70 / 40 | Yes
B10 | Unconditioned (stairs, shafts, storage, parking) | 1 | zone06 |  |  | 0 | OccSch_<room> (lecture timetable) | 6 | LghSch_Costant | 2 | EqpSch_Costant |  |  | 100 / 0 | No
B10 | Conditioned service / circulation | 2 | zone08, zone13 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  | 70 / 40 | Yes
B10 | Conditioned service / circulation | 1 | zone09 |  |  | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | EqpSch_Unoccupied |  |  | 70 / 40 | Yes
B10 | Snack bar | 1 | zone12 |  |  | 0.8 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | EqpSch_Unoccupied |  |  | 70 / 40 | Yes
B10 | Research laboratory | 1 | zone14 |  |  | 0.3 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | EqpSch_Unoccupied |  |  | 70 / 40 | Yes
B10 | Lecture hall / study room | 4 | zone15, zone16, zone18, zone19 |  |  | 0.6 | OccSch_<room> (lecture timetable) | 6 | LghSch_<room> (lecture timetable) | 10 | EqpSch_<room> (lecture timetable) |  |  | 70 / 40 | Yes
Note on A1: Condensed version of T7_Zones for the manuscript: zones with identical loads, schedules and ventilation status are grouped. Area, occupants and OA are SUMIFS over T7_Zones via the zone list key in column D.

## T8_Envelope
Construction | Envelope role | Include in paper | Source | N layers | Layers outside → inside: material, thickness (λ W/m·K; ρ kg/m³; c J/kg·K) | Layer data from | Total thickness (m) | R layers (m²K/W) | Rsi (m²K/W) | Rse (m²K/W) | U (W/m²K) | B09 net opaque area (m²) | B09 N surfaces | B10 net opaque area (m²) | B10 N surfaces
WL_POLIMI-LC_EW01 | External wall | Yes | IFC IfcMaterialLayerSet | 8 | Pannello in alluminio 0.5 cm (λ 220; ρ 2700; c 896) ¦ Camera d'aria fortemente ventilata 3.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante rigido 6 cm (λ 0.04; ρ 30; c 1452) ¦ Membrana impermeabilizzante 0.5 cm (λ 0.23; ρ 1100; c 1000) ¦ Camera d'aria debolmente ventilata 20 cm (λ 1; ρ 1; c 1004) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 89.5 | 3 | 98.6 | 3
WL_POLIMI-LC_EW02 | External wall | Yes | IFC IfcMaterialLayerSet; also fallback for unmatched exterior faces | 8 | Pannello in alluminio 0.5 cm (λ 220; ρ 2700; c 896) ¦ Camera d'aria fortemente ventilata 3.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante rigido 10 cm (λ 0.04; ρ 30; c 1452) ¦ Membrana impermeabilizzante 0.5 cm (λ 0.23; ρ 1100; c 1000) ¦ Camera d'aria debolmente ventilata 26 cm (λ 1; ρ 1; c 1004) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 2427.6 | 156 | 531.9 | 33
WL_POLIMI-LC_EW03 | External wall | Yes | IFC IfcMaterialLayerSet | 9 | Pannello in alluminio 0.5 cm (λ 220; ρ 2700; c 896) ¦ Camera d'aria fortemente ventilata 3.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante rigido 10 cm (λ 0.04; ρ 30; c 1452) ¦ Membrana impermeabilizzante 0.5 cm (λ 0.23; ρ 1100; c 1000) ¦ Camera d'aria debolmente ventilata 26.5 cm (λ 1; ρ 1; c 1004) ¦ CLS 42.5 cm (λ 1.046; ρ 2300; c 657) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 179.4 | 13 | 214 | 8
WL_POLIMI-LC_EW04 | External wall | Yes | IFC IfcMaterialLayerSet | 7 | Pannello in alluminio 0.5 cm (λ 220; ρ 2700; c 896) ¦ Camera d'aria fortemente ventilata 3.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante rigido 10 cm (λ 0.04; ρ 30; c 1452) ¦ Membrana impermeabilizzante 0.5 cm (λ 0.23; ρ 1100; c 1000) ¦ Camera d'aria debolmente ventilata 26.5 cm (λ 1; ρ 1; c 1004) ¦ CLS 42.5 cm (λ 1.046; ρ 2300; c 657) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 250.3 | 11 | 12.3 | 1
WL_POLIMI-LC_EW05 | External wall | Yes | IFC IfcMaterialLayerSet | 9 | Pannello in alluminio 0.5 cm (λ 220; ρ 2700; c 896) ¦ Camera d'aria fortemente ventilata 3.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante rigido 10 cm (λ 0.04; ρ 30; c 1452) ¦ Membrana impermeabilizzante 0.5 cm (λ 0.23; ρ 1100; c 1000) ¦ Camera d'aria debolmente ventilata 26.5 cm (λ 1; ρ 1; c 1004) ¦ Camera d'aria fortemente ventilata 42.5 cm (λ 0.285; ρ 1; c 1004) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 493.4 | 34 | 108 | 2
WL_POLIMI-LC_FC300 | External wall | Yes | IFC IfcMaterialLayerSet | 3 | Intonaco interno 1.5 cm (λ 0.35; ρ 1200; c 999) ¦ Calcestruzzo- gettato in opera 26 cm (λ 1.046; ρ 2300; c 657) ¦ Intonaco interno 1.5 cm (λ 0.35; ρ 1200; c 999) | B10 |  |  | 0.13 | 0.04 |  | 0 | 0 | 190.2 | 15
WL_POLIMI-LC_FC300-2 | External wall | Yes | IFC IfcMaterialLayerSet | 5 | Intonaco interno 1.5 cm (λ 0.35; ρ 1200; c 999) ¦ Calcestruzzo- gettato in opera 26 cm (λ 1.046; ρ 2300; c 657) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 1131.6 | 48 | 0 | 0
WL_POLIMI-LC_FC300-3 | External wall | Yes | IFC IfcMaterialLayerSet | 8 | Intonaco interno 1.5 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 10 cm (λ 0.04; ρ 80; c 1028) ¦ Camera d'aria debolmente ventilata 15 cm (λ 1; ρ 1; c 1004) ¦ Calcestruzzo- gettato in opera 26 cm (λ 1.046; ρ 2300; c 657) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.04 |  | 4.8 | 1 | 0 | 0
RF_POLIMI-LC_IH-E | Roof | Yes | Notebook (manual layers) | 4 | Ghiaia 8 cm (λ 1.2; ρ 1700; c 1000) ¦ Massetto 12 cm (λ 1.2; ρ 1700; c 1000) ¦ Isolante rigido 8 cm (λ 0.04; ρ 30; c 1452) ¦ CLS 25 cm (λ 1.046; ρ 2300; c 657) | B09 |  |  | 0.1 | 0.04 |  | 4003 | 52 | 1590.2 | 17
FL_POLIMI-LC_GroundFloor | Ground floor | Yes | IFC IfcMaterialLayerSet | 7 | Pavimento industriale 6 cm (λ 1.046; ρ 2300; c 657) ¦ Massetto 8 cm (λ 1.2; ρ 1700; c 1000) ¦ Isolante rigido 6 cm (λ 0.04; ρ 30; c 1452) ¦ CLS 5 cm (λ 1.046; ρ 2300; c 657) ¦ Camera d'aria fortemente ventilata 35 cm (λ 0.285; ρ 1; c 1004) ¦ Magrone 10 cm (λ 1.046; ρ 2300; c 657) ¦ Ghiaia 20 cm (λ 1.2; ρ 1700; c 1000) | B09 |  |  | 0.17 | 0 |  | 2621.2 | 46 | 196.9 | 15
Generic Ground Slab | Ground floor | Yes | HB default (no BIM match) | 2 | Generic 50mm Insulation 5 cm (λ 0.03; ρ 43; c 1210) ¦ Generic HW Concrete 20 cm (λ 1.95; ρ 2240; c 900) | B09 |  |  | 0.17 | 0 |  | 1381.7 | 1 | 0 | 0
FL_POLIMI-LC_InternalFloor_IH-E | Floor over outdoor/unheated | Yes | IFC IfcMaterialLayerSet | 5 | Linoleum 1 cm (λ 0.041; ρ 50; c 2301) ¦ Massetto 15 cm (λ 1.2; ρ 1700; c 1000) ¦ Isolante rigido 10 cm (λ 0.04; ρ 30; c 1452) ¦ Solaio laterocemento 15 cm (λ 0.66; ρ 1100; c 839) ¦ Intonaco interno 2 cm (λ 0.35; ρ 1200; c 999) | B10 |  |  | 0.17 | 0.04 |  | 0 | 0 | 1393.3 | 13
WL_POLIMI-LC_IW01 | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 6 | Intonaco gesso puro 1 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Camera d'aria non ventilata 4 cm (λ 1; ρ 1; c 1003) ¦ Calcestruzzo armato 30 cm (λ 2.3; ρ 2399.96; c 1000) ¦ Intonaco interno 2 cm (λ 0.35; ρ 1200; c 999) | B10 |  |  | 0.13 | 0.13 |  | 0 | 0 | 125.2 | 3
WL_POLIMI-LC_IW02 | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 7 | Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Camera d'aria non ventilata 6.5 cm (λ 1; ρ 1; c 1003) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco gesso puro 1 cm (λ 0.35; ρ 1200; c 999) | B09 |  |  | 0.13 | 0.13 |  | 73 | 2 | 296.1 | 20
WL_POLIMI-LC_IW03 | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 3 | Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 6.5 cm (λ 0.04; ρ 80; c 1028) | B09 |  |  | 0.13 | 0.13 |  | 1538.1 | 135 | 237.8 | 14
WL_POLIMI-LC_IW04 | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 8 | Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Camera d'aria non ventilata 6.5 cm (λ 1; ρ 1; c 1003) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco gesso puro 1 cm (λ 0.35; ρ 1200; c 999) ¦ Piastrelle 1.5 cm (λ 1.3; ρ 2300; c 839) | B10 |  |  | 0.13 | 0.13 |  | 0 | 0 | 33.5 | 2
WL_POLIMI-LC_IW05_Toilet | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 9 | Piastrelle 1.5 cm (λ 1.3; ρ 2300; c 839) ¦ Intonaco interno 1 cm (λ 0.35; ρ 1200; c 999) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Camera d'aria non ventilata 6.5 cm (λ 1; ρ 1; c 1003) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco gesso puro 1 cm (λ 0.35; ρ 1200; c 999) ¦ Piastrelle 1.5 cm (λ 1.3; ρ 2300; c 839) | B09 |  |  | 0.13 | 0.13 |  | 190.1 | 16 | 112.4 | 7
WL_POLIMI-LC_IW06_Toilet | Internal partition exposed to outdoors (adjacent cell excluded from BEM) | No | IFC IfcMaterialLayerSet | 5 | Camera d'aria non ventilata 6.5 cm (λ 1; ρ 1; c 1003) ¦ Isolante morbido 4 cm (λ 0.04; ρ 80; c 1028) ¦ Gypsum Board 2.5 cm (λ 0.21; ρ 900; c 1000) ¦ Intonaco gesso puro 1 cm (λ 0.35; ρ 1200; c 999) ¦ Piastrelle 1.5 cm (λ 1.3; ρ 2300; c 839) | B09 |  |  | 0.13 | 0.13 |  | 295.6 | 21 | 85.2 | 4
Note on A1: Proposed Appendix Table 8: every construction assigned to a surface with Outdoors, Ground or Adiabatic boundary in the calibrated IDFs (constructions are identical in baseline and calibrated, and in both buildings).
Note on C1: 'No' = interior partition that is exterior only because neighbouring cells were excluded from the BEM; suggested to mention in a footnote rather than list.
Note on J1: Input (blue): ISO 6946 surface resistances by category; ground floor Rse = 0 (soil excluded).
Note on M1: Gross area of the surfaces minus the windows they host; boundary Outdoors + Ground + Adiabatic.

## T9_Glazing
Construction | Element | E+ model | U (W/m²K) | SHGC | VT | Glass layers (BIM) | Glass U (BIM, W/m²K) | Frame material (BIM) | Frame U (BIM, W/m²K) | Glazing area fraction (BIM) | Glazed fraction in BEM | B09 N surfaces | B09 area (m²) | B09 with ext. blind | B10 N surfaces | B10 area (m²) | B10 with ext. blind | Note
windowConstruction_U0.9_SHGC0.67_VT0.8 | Window / glazed door (IfcWindow, IfcDoor) | WindowMaterial:SimpleGlazingSystem | 0.9 | 0.67 | 0.8 | Double | 1.1 | Aluminium | 0.7 | 0.8 | geometry of the aperture | 1 | 3.8 | 0 | 2 | 23 | 1
curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.8 | Curtain wall (IfcWall CurtainWall / CurtainWall150) | WindowMaterial:SimpleGlazingSystem | 0.9 | 0.67 | 0.8 | Double | 1.1 | Aluminium | 0.7 | 0.8 | 0.81 (face scaled 0.9 × 0.9) | 31 | 1061 | 11 | 12 | 611.3 | 1
windowConstruction_U0.9_SHGC0.67_VT0.58 | Window / glazed door (IfcWindow, IfcDoor) | WindowMaterial:SimpleGlazingSystem | 0.9 | 0.67 | 0.58 | Double | 1.1 | Aluminium | 0.7 | 0.8 | geometry of the aperture | 0 | 0 | 0 | 2 | 7.6 | 0
curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.58 | Curtain wall (IfcWall CurtainWall / CurtainWall150) | WindowMaterial:SimpleGlazingSystem | 0.9 | 0.67 | 0.58 | Double | 1.1 | Aluminium | 0.7 | 0.8 | 0.81 (face scaled 0.9 × 0.9) | 23 | 841.5 | 0 | 9 | 478.8 | 2 | B09: 23 curtain-wall panels (841.5 m²) have BIM VT 0.58 but kept HB 'Generic Double Pane' in the IDF; reported here with their BIM glazing properties (author decision, table only).
Note on A1: Proposed Appendix Table 9 (calibrated IDFs; glazing unchanged by calibration). Only U, SHGC and VT enter E+; glass/frame properties are BIM data not used by the simple glazing model.
Note on O1: External aluminium blinds: slat 0.30 m, separation 0.50 m, angle 90°, solar reflectance 0.6, always on (see Map_Apertures A14).

## Map_Spaces
ID | Paper table | Paper property name | Topologic entity | Topologic key | IFC entity | IFC pset | IFC property | Read by workflow from | BIM unit | Cell → zone aggregation | Honeybee object | Honeybee attribute | EnergyPlus object | EnergyPlus field | E+ unit | Conversion BIM → E+ | Default if missing / 'Undefined' | In IDF? | Implementation | Value B09 (BIM) | Value B10 (BIM) | Value in IDF – baseline | Value in IDF – calibrated | Notes
S01 | T7 | Occupancy Type | Cell | pr_OccupancyType | IfcSpace | Altro (B09) / Other (B10) | pr_OccupancyType | Topologic JSON | text | Prevalent: type of the cell with the largest occupant count (density × area) | Room | properties.energy.program_type (fixed: honeybee_energy office_program, not mapped) | People / Lights / ElectricEquipment / ZoneInfiltration:DesignFlowRate | Name (prefix 'Generic Office …' inherited from HB office program) | – | none | 'StorageSpaces:GeneralStorageSpace' (cell, B09 nb); 'FacilityServiceSpaces:Corridor' if zone type contains 'Default' (B09 nb) | No | Utils.TopologicZoneInheritSpaceData (Operation.py:4); TBIM.Cells_ClusterizeIntoEnergyZones | FacilityServiceSpaces:HorizontalInfrastructure/ServiceSpaceNon-Occupied (×56); EducationandTrainingSpaces:Research/Non-ClassClassLaboratory (×23); EducationandTrainingSpaces:LectureHall(FixedSeats) (×19); FacilityServiceSpaces:UtilityEquipmentRoom (×13); FacilityServiceSpaces:ElevatorShaft (×12); FacilityServiceSpaces:Restroom (×12); FacilityServiceSpaces:Stairway (×9); FacilityServiceSpaces:Corridor (×8); StorageSpaces:GeneralStorageSpace (×1); EducationandTrainingSpaces:StudyRoom (×1); CommerceActivitySpaces:OfficeSpaces (×1) | FacilityServiceSpaces:Corridor (×8); FacilityServiceSpaces:HorizontalInfrastructure/ServiceSpaceNon-Occupied (×8); FacilityServiceSpaces:Restroom (×7); FacilityServiceSpaces:Stairway (×5); FacilityServiceSpaces:ElevatorShaft (×5); EducationandTrainingSpaces:LectureHall(FixedSeats) (×4); ParkingSpaces:InteriorParkingSpaces (×3); FacilityServiceSpaces:UtilityEquipmentRoom (×3); StorageSpaces:GeneralStorageSpace (×3); ServiceActivitySpaces:SnackBar (×1); EducationandTrainingSpaces:Research/Non-ClassClassLaboratory (×1); ProtectiveSpaces:EntryPorch (×1) | not written | not written | Used only to build zones: single-cell zones for lecture halls, labs, storage; stairs/elevators merged with adjacent corridor; horizontal infrastructure merged with corridor/stair/restroom.
S02 | T7 | Is Occupied | Cell | pr_IsOccupied | IfcSpace | Altro (B09) / Other (B10) | pr_IsOccupied | Topologic JSON | bool (0/1) | Logical OR | – | – | – | – | – | none | 0 | No | TBIM.Cells_ClusterizeIntoEnergyZones (K-Means feature) | 0 / 1 | 0 / 1 | – | – | K-Means feature (standardised).
S03 | T7 | Is Heated | Cell | pr_IsHeated | IfcSpace | Altro (B09) / Other (B10) | pr_IsHeated | Topologic JSON | bool (0/1) | Logical OR | – | – | – | – | – | none | 0 | No | TBIM.Cells_ClusterizeIntoEnergyZones (K-Means feature) | 0 / 1 | 0 / 1 | – | – | Heating availability in E+ comes from rl_IsScheduledBy_Heating (S29), not from this flag.
S04 | T7 | Is Cooled | Cell | pr_IsCooled | IfcSpace | Altro (B09) / Other (B10) | pr_IsCooled | Topologic JSON | bool (0/1) | Logical OR | – | – | – | – | – | none | 0 | No | TBIM.Cells_ClusterizeIntoEnergyZones (K-Means feature) | 0 / 1 | 0 / 1 | – | – | Cooling availability in E+ comes from rl_IsScheduledBy_Cooling (S30).
S05 | T7 | Is Mechanically Ventilated | Cell | pr_IsMechanicallyVentilated | IfcSpace | Altro (B09) / Other (B10) | pr_IsMechanicallyVentilated | Topologic JSON | bool (0/1) | Logical OR (stored on zone) | – | – | – | – | – | none | – | No | Utils.TopologicZoneInheritSpaceData (Operation.py:4) | 0 / 1 | 0 / 1 | – | – | TBIM also contains a duplicate key 'pr_IsMechanicalVentilated'.
S06 | T7 | Is Naturally Ventilated | Cell | pr_IsNaturallyVentilated | IfcSpace | Altro (B09) / Other (B10) | pr_IsNaturallyVentilated | not read | bool (0/1) | – | – | – | – | – | – | – | – | No | – | 0 | 0 / 1 | – | – | No natural-ventilation object (ZoneVentilation) is generated.
S07 | T7 | Artificial Lighting | Cell | pr_ArtificialLighting | IfcSpace | Altro (B09) / Other (B10) | pr_ArtificialLighting | not read | bool (0/1) | – | – | – | – | – | – | – | – | No | – | 1 | 1 | – | –
S08 | T7 | Illuminance | Cell | pr_Illuminance | IfcSpace | Altro (B09) / Other (B10) | pr_Illuminance | not read | lux | – | – | – | Lights | Lighting_Level (= Design Level, W) hard-coded 300 | W | none | – | No | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 150 / 200 / 300 / 500; Undefined (×12) | 150 / 200 / 300 / 500; Undefined (×7) | 300 written in Lighting_Level but ignored (method = Watts/Area) | same | The 300 is not lux: in E+ 'Lighting Level' is a power in W and is unused when Design Level Calculation Method = Watts/Area.
S09 | T7 | Lighting Power Density | Cell | pr_LightingPowerDensity | IfcSpace | Altro (B09) / Other (B10) | pr_LightingPowerDensity | Topologic JSON | W/m² | Area-weighted mean | Room → Lighting (from office program, then overwritten in IDF) | properties.energy.lighting.watts_per_area | Lights | Watts_per_Floor_Area (Design Level Calculation Method = Watts/Area) | W/m² | 1:1 | 0 | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 6 / 7 | 6 | B09: 0 / 6 / 7 ¦ B10: 6 | B09: 0 / 6 / 7 ¦ B10: 6 | Return-air 0, radiant 0.7, visible 0.2 (HB office defaults).
S10 | T7 | Lighting Level | – | (not in TBIM) | – | – | – | – | W | – | – | – | Lights | Design_Level | W | – | – | No | – | – | – | computed internally by E+ (W/m² × floor area) | same | Paper says 'Calculate from Power Density · Area'; this is done by E+, not by the workflow.
S11 | T7 | Equipment Power Density | Cell | pr_EquipmentPowerDensity | IfcSpace | Altro (B09) / Other (B10) | pr_EquipmentPowerDensity | Topologic JSON | W/m² | Area-weighted mean | Room → ElectricEquipment (office program, overwritten in IDF) | properties.energy.electric_equipment.watts_per_area | ElectricEquipment | Watts_per_Floor_Area (method Watts/Area) | W/m² | 1:1 | 0 ('Undefined' → 0 in TBIM.Cells_CleanUndefinedData) | Partial | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | Undefined | 0; Undefined (×46) | B09: 0 ¦ B10: 0 | B09: 0 / 2 ¦ B10: 0 / 2 / 10 | Undefined in the TBIM for every space → 0 W/m² in the baseline; 2 and 10 W/m² were typed manually during calibration.
S12 | T7 | Occupancy Density Operation | Cell | pr_OccupancyDensityOperation | IfcSpace | Altro (B09) / Other (B10) | pr_OccupancyDensityOperation | Topologic JSON | pp/m² | Area-weighted mean | Room → People (office program, overwritten in IDF) | properties.energy.people.people_per_area | People | People_per_Floor_Area (Number of People Calculation Method = People/Area) | person/m² | 1:1 | 0 | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 0 / 0.12 / 0.3 / 0.6; Undefined (×12) | 0 / 0.3 / 0.6 / 0.8; Undefined (×10) | B09: 0 / 0.12 / 0.3 / 0.6 ¦ B10: 0 / 0.3 / 0.6 / 0.8 | B09: 0 / 0.12 / 0.3 / 0.6 ¦ B10: 0 / 0.3 / 0.6 / 0.8 | Activity schedule 'Seated Adult Activity', radiant fraction 0.3 (HB office defaults). Also a K-Means feature.
S13 | T7 | Occupancy Density Safety | Cell | pr_OccupancyDensitySafety | IfcSpace | Altro (B09) / Other (B10) | pr_OccupancyDensitySafety | Topologic JSON | pp/m² | Area-weighted mean (stored on zone) | – | – | – | – | – | none | 0 | No | Utils.TopologicZoneInheritSpaceData (Operation.py:4) | 0 / 0.4 / 1.2 | 0 / 0.01 / 0.4 / 0.7 / 1.2 | – | – | Fire-safety design density; not an energy input.
S14 | T7 | Occupancy Number | Cell | pr_OccupancyNumber / pr_OccupancyNumberPeak | IfcSpace | Altro (B09) / Other (B10) | pr_OccupancyNumberPeak | not read | pp | – | – | – | – | – | – | – | – | No | – | 16–158 (10 distinct); None (×122) | 49 / 126 / 162 / 180; None (×45) | – | – | Present only on some cells. Occupant count in E+ = People/Area × floor area × schedule.
S15 | T7 | Mechanical Ventilation Rate | Cell | pr_MechanicalVentilationRate | IfcSpace | Altro (B09) / Other (B10) | pr_MechanicalVentilationRate | Topologic JSON | h⁻¹ per paper; used as L/s·m² by code | Code intends volume-weighted mean, but zone value = value of LAST cell iterated (Operation.py:170 writes pr_MechanicalVentilationRate, not pr_ZoneMechanicalVentilationRate) | Room → Ventilation (office program, overwritten in IDF) | properties.energy.ventilation.flow_per_area | DesignSpecification:OutdoorAir | Outdoor_Air_Flow_per_Zone_Floor_Area (Outdoor Air Method = Maximum) | m³/s·m² | ÷ 1000 | 0 | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 0–1332.16 (60 distinct) | 0–8 (9 distinct); Undefined (×3) | B09: 0–0.008 (38 distinct) ¦ B10: 0–0.008 (9 distinct) | B09: 0–0.008 (38 distinct) ¦ B10: 0–0.008 (9 distinct) | Stored value is an air-change rate (h⁻¹) = N_peak × 7 L/s·p × 3.6 / V_net, but the code writes it as L/s·m² (see I07). Restrooms: 8 h⁻¹ → 0.008 m³/s·m².
S16 | T7 | Mechanical Ventilation Rate Per Person | Cell | pr_MechanicalVentilationRatePerPerson | IfcSpace | Altro (B09) / Other (B10) | (only in TBIM JSON) | Topologic JSON | L/s·person | Occupant-weighted mean | Room → Ventilation | properties.energy.ventilation.flow_per_person | DesignSpecification:OutdoorAir | Outdoor_Air_Flow_per_Person | m³/s·person | ÷ 1000 | 0 | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 0 / 7 | 0 / 7 | B09: 0 / 0.007 ¦ B10: 0 / 0.007 | B09: 0 / 0.007 ¦ B10: 0 / 0.007 | Referenced by HVACTemplate:Zone:IdealLoadsAirSystem (Outdoor Air Method = DetailedSpecification). 'Maximum' = max(per-person, per-area), not their sum.
S17 | T7 | Mechanical Ventilation Rate Per Volume | Cell | pr_MechanicalVentilationRatePerVolume | IfcSpace | Altro (B09) / Other (B10) | pr_MechanicalVentilationRatePerVolume | Topologic JSON | h⁻¹ | – | – | – | – | – | – | none | 0 | No | TBIM.Cells_CleanUndefinedData only | 0 / 1 / 8 | 0 / 1 / 8 | – | – | For stairs/elevators/restrooms the same number is also stored in pr_MechanicalVentilationRate, which is what reaches E+.
S18 | T7 | Natural Ventilation Rate | – | (not in TBIM) | – | – | – | notebook constant | – | – | – | – | ZoneInfiltration:DesignFlowRate | see Map_Model M16 | – | – | – | No | – | – | – | – | – | Paper reports 0.30 h⁻¹ 'baseline envelope infiltration'; the model uses 0.0001 m³/s per m² of exterior surface (see M16 / I09).
S19 | T7 | Space Temperature Summer Max | Cell | pr_SpaceTemperatureSummerMax | IfcSpace | Altro (B09) / Other (B10) | pr_SpaceTemperatureSummerMax | Topologic JSON | °C | Minimum over cells (stored on zone) | Room → Setpoint | cooling_schedule = ScheduleRuleset.from_constant_value('Generic room Cooling', 26) – NOT from TBIM | HVACTemplate:Thermostat → Schedule | Cooling_Setpoint_Schedule_Name = 'Generic room Cooling' | °C | none | 26 (B09 nb) / 30 (TBIM.Cells_CleanUndefinedData) | No | HB.HBRoomSetSetpointSchedules (Operation.py:541) | 26; Undefined (×21) | 26; Undefined (×14) | Schedule:Constant 26 °C (both buildings) | Schedule:Compact 20 °C (B09) / 22 °C (B10), all day | TBIM temperature limits are not transferred; see Issues I04.
S20 | T7 | Space Temperature Summer Min | Cell | pr_SpaceTemperatureSummerMin | IfcSpace | Altro (B09) / Other (B10) | pr_SpaceTemperatureSummerMin | Topologic JSON | °C | Minimum over cells (stored on zone) | – | – | – | – | – | none | 23 (B09 nb) / 28 (CleanUndefinedData) | No | Utils.TopologicZoneInheritSpaceData (Operation.py:4) | 23; Undefined (×21) | 23; Undefined (×14) | – | –
S21 | T7 | Space Temperature Winter Max | Cell | pr_SpaceTemperatureWinterMax | IfcSpace | Altro (B09) / Other (B10) | pr_SpaceTemperatureWinterMax | Topologic JSON | °C | Maximum over cells (stored on zone) | – | – | – | – | – | none | 23.5 (B09 nb) / 16 (CleanUndefinedData) | No | Utils.TopologicZoneInheritSpaceData (Operation.py:4) | 23.5; Undefined (×21) | 23.5; Undefined (×14) | – | –
S22 | T7 | Space Temperature Winter Min | Cell | pr_SpaceTemperatureWinterMin | IfcSpace | Altro (B09) / Other (B10) | pr_SpaceTemperatureWinterMin | Topologic JSON | °C | Maximum over cells (stored on zone) | Room → Setpoint | heating_schedule = constant 'Generic room Heating' 20 °C – NOT from TBIM | HVACTemplate:Thermostat → Schedule | Heating_Setpoint_Schedule_Name = 'Generic room Heating' | °C | none | 18 (B09 nb) / 10 (CleanUndefinedData) | No | HB.HBRoomSetSetpointSchedules | 18; Undefined (×21) | 18; Undefined (×14) | Schedule:Constant 20 °C | B09: 15 °C (0–7 h) / 18 °C (7–18 h) / 15 °C; B10: 18 / 22 / 18 °C | See Issues I04.
S23 | T7 | Space Humidity Max | Cell | pr_HumidityMax | IfcSpace | Altro (B09) / Other (B10) | pr_HumidityMax | Topologic JSON | % RH | Minimum over cells | Room → IdealAirSystem (add_default_ideal_air) | – (written after export) | HVACTemplate:Zone:IdealLoadsAirSystem | Dehumidification_Setpoint (Dehumidification Control Type = Humidistat) | % RH | 1:1 | 100 (TBIM.Cells_CleanUndefinedData) | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 70; Undefined (×12) | 70; Undefined (×11) | B09: 70 / 100 ¦ B10: 70 / 100 | B09: 70 / 100 ¦ B10: 70 / 100 | HB also writes unused constant schedules 'Generic room Dehumidifying' 60 % / 'Generic room Humidifying' 10 %.
S24 | T7 | Space Humidity Min | Cell | pr_HumidityMin | IfcSpace | Altro (B09) / Other (B10) | pr_HumidityMin | Topologic JSON | % RH | Maximum over cells | Room → IdealAirSystem | – | HVACTemplate:Zone:IdealLoadsAirSystem | Humidification_Setpoint (Humidification Control Type = Humidistat) | % RH | 1:1 | 0 | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | 40; Undefined (×12) | 40; Undefined (×11) | B09: 0 / 40 ¦ B10: 0 / 40 | B09: 0 / 40 ¦ B10: 0 / 40
S25 | T7 | Space Wind Load Rating | Cell | pr_SpaceWindLoadRating | IfcSpace | Altro (B09) / Other (B10) | pr_SpaceWindLoadRating | not read | class | – | – | – | – | – | – | – | – | No | – | Undefined (×67); A4 (×59); None (×29) | Undefined (×33); None (×12); A4 (×4) | – | – | Paper says 'Eurocode 1 / Class 3'; the model stores window class 'A4' (EN 12210).
S26 | – (new) | Occupancy schedule | Cell (added by nb) | rl_IsScheduledBy_Occupancy | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Occupancy | IFC DesignTransferView | schedule id | Value of LAST cell iterated (Operation.py:174 uses rl_IsScheduledBy_*, not rl_ZoneIsScheduledBy_*) | Room → People | occupancy_schedule (overwritten in IDF) | People | Number_of_People_Schedule_Name | – | id; prefix 'OccSch_' | 'OccSch_Unoccupied' | Yes | scripts/01_bim_to_bem.py+ TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×71); OccSch_Unoccupied (×67); OccSch_B0.1 (×2); OccSch_B0.7 (×1); OccSch_B0.6 (×1); OccSch_B0.5 (×1); OccSch_B1.3 (×1); OccSch_B0.4 (×1); OccSch_B0.3 (×1); OccSch_B0.2 (×1); OccSch_B1.5 (×1); OccSch_B1.4 (×1); OccSch_B1.2 (×1); OccSch_B1.1 (×1); OccSch_B2.4 (×1); OccSch_B2.3 (×1); OccSch_B2.6 (×1); OccSch_B2.5 (×1); OccSch_B2.2 (×1) | OccSch_Unoccupied (×31); None (×13); OccSch_A0.1/A0.2 (×2); OccSch_A1.3 (×1); OccSch_A1.2 (×1); OccSch_A1.1 (×1) | B09: OccSch_Unoccupied (×47); OccSch_B0.1 (×2); OccSch_B0.7 (×1); OccSch_B0.6 (×1); OccSch_B0.5 (×1); OccSch_B1.3 (×1); OccSch_B0.4 (×1); OccSch_B0.3 (×1); OccSch_B0.2 (×1); OccSch_B1.5 (×1); OccSch_B1.4 (×1); OccSch_B1.2 (×1); OccSch_B1.1 (×1); OccSch_B2.3 (×1); OccSch_B2.4 (×1); OccSch_B2.6 (×1); OccSch_B2.5 (×1); OccSch_B2.2 (×1) ¦ B10: OccSch_Unoccupied (×15); OccSch_A0.1/A0.2 (×2); OccSch_A1.3 (×1); OccSch_A1.2 (×1); OccSch_A1.1 (×1) | B09: OccSch_Unoccupied (×47); OccSch_B0.1 (×2); OccSch_B0.7 (×1); OccSch_B0.6 (×1); OccSch_B0.5 (×1); OccSch_B1.3 (×1); OccSch_B0.4 (×1); OccSch_B0.3 (×1); OccSch_B0.2 (×1); OccSch_B1.5 (×1); OccSch_B1.4 (×1); OccSch_B1.2 (×1); OccSch_B1.1 (×1); OccSch_B2.3 (×1); OccSch_B2.4 (×1); OccSch_B2.6 (×1); OccSch_B2.5 (×1); OccSch_B2.2 (×1) ¦ B10: OccSch_Unoccupied (×15); OccSch_A0.1/A0.2 (×2); OccSch_A1.3 (×1); OccSch_A1.2 (×1); OccSch_A1.1 (×1) | Schedules defined in _schedules/Schedules_Occupancy_PoliMi_LC.json (see Val_Schedules).
S27 | – (new) | Lighting schedule | Cell (added by nb) | rl_IsScheduledBy_Lighting | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Lighting | IFC DesignTransferView | schedule id | Value of last cell iterated | Room → Lighting | schedule (overwritten in IDF) | Lights | Schedule_Name | – | first token before ';' | 'AlwaysOff' (cell); 'LghSch_Costant' (B09 zone fix) | Yes | scripts/01_bim_to_bem.py+ TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×71); LghSch_Costant (×53); LghSch_Unoccupied (×14); LghSch_Costant;LghSch_B0.1 (×2); LghSch_Costant;LghSch_B0.7 (×1); LghSch_Costant;LghSch_B0.6 (×1); LghSch_Costant;LghSch_B0.5 (×1); LghSch_Costant;LghSch_B1.3 (×1); LghSch_Costant;LghSch_B0.4 (×1); LghSch_Costant;LghSch_B0.3 (×1); LghSch_Costant;LghSch_B0.2 (×1); LghSch_Costant;LghSch_B1.5 (×1); LghSch_Costant;LghSch_B1.4 (×1); LghSch_Costant;LghSch_B1.2 (×1); LghSch_Costant;LghSch_B1.1 (×1); LghSch_Costant;LghSch_B2.4 (×1); LghSch_Costant;LghSch_B2.3 (×1); LghSch_Costant;LghSch_B2.6 (×1); LghSch_Costant;LghSch_B2.5 (×1); LghSch_Costant;LghSch_B2.2 (×1) | LghSch_Unoccupied (×16); LghSch_Costant (×15); None (×14); LghSch_A1.3;LghSch_Costant (×1); LghSch_A1.2;LghSch_Costant (×1); LghSch_A1.1;LghSch_Costant (×1); LghSch_A0.1/A0.2;LghSch_Costant (×1) | B09: LghSch_Costant (×55); AlwaysOff (×9); LghSch_Unoccupied (×1) ¦ B10: LghSch_Costant (×7); AlwaysOff (×5); LghSch_Unoccupied (×4); LghSch_A1.3 (×1); LghSch_A1.2 (×1); LghSch_A1.1 (×1); LghSch_A0.1/A0.2 (×1) | B09: LghSch_Costant (×55); AlwaysOff (×9); LghSch_Unoccupied (×1) ¦ B10: LghSch_Costant (×7); AlwaysOff (×5); LghSch_Unoccupied (×4); LghSch_A1.3 (×1); LghSch_A1.2 (×1); LghSch_A1.1 (×1); LghSch_A0.1/A0.2 (×1) | Multi-valued IFC entries such as 'LghSch_Costant;LghSch_B0.1' keep only the FIRST id. 'LghSch_Costant' = 0 all year in the baseline (see I06).
S28 | – (new) | Equipment schedule | Cell (added by nb) | rl_IsScheduledBy_Equipment | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Equipment | IFC DesignTransferView | schedule id | Value of last cell iterated | Room → ElectricEquipment | schedule (overwritten in IDF) | ElectricEquipment | Schedule_Name | – | first token before ';' | 'AlwaysOff' (cell); 'EqpSch_Unoccupied' (B09 zone fix) | Yes | scripts/01_bim_to_bem.py+ TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×71); EqpSch_Costant (×53); EqpSch_Unoccupied (×14); EqpSch_Costant;EqpSch_B0.1 (×2); EqpSch_Costant;EqpSch_B0.7 (×1); EqpSch_Costant;EqpSch_B0.6 (×1); EqpSch_Costant;EqpSch_B0.5 (×1); EqpSch_Costant;EqpSch_B1.3 (×1); EqpSch_Costant;EqpSch_B0.4 (×1); EqpSch_Costant;EqpSch_B0.3 (×1); EqpSch_Costant;EqpSch_B0.2 (×1); EqpSch_Costant;EqpSch_B1.5 (×1); EqpSch_Costant;EqpSch_B1.4 (×1); EqpSch_Costant;EqpSch_B1.2 (×1); EqpSch_Costant;EqpSch_B1.1 (×1); EqpSch_Costant;EqpSch_B2.4 (×1); EqpSch_Costant;EqpSch_B2.3 (×1); EqpSch_Costant;EqpSch_B2.6 (×1); EqpSch_Costant;EqpSch_B2.5 (×1); EqpSch_Costant;EqpSch_B2.2 (×1) | EqpSch_Costant (×18); None (×14); EqpSch_Unoccupied (×13); EqpSch_A1.3;EqpSch_Costant (×1); EqpSch_A1.2;EqpSch_Costant (×1); EqpSch_A1.1;EqpSch_Costant (×1); EqpSch_A0.1/A0.2;EqpSch_Costant (×1) | B09: EqpSch_Costant (×55); AlwaysOff (×9); EqpSch_Unoccupied (×1) ¦ B10: EqpSch_Costant (×6); EqpSch_Unoccupied (×5); AlwaysOff (×5); EqpSch_A1.3 (×1); EqpSch_A1.2 (×1); EqpSch_A1.1 (×1); EqpSch_A0.1/A0.2 (×1) | B09: EqpSch_Costant (×55); AlwaysOff (×9); EqpSch_Unoccupied (×1) ¦ B10: EqpSch_Costant (×6); EqpSch_Unoccupied (×5); AlwaysOff (×5); EqpSch_A1.3 (×1); EqpSch_A1.2 (×1); EqpSch_A1.1 (×1); EqpSch_A0.1/A0.2 (×1) | 'EqpSch_Costant' (sic) is a copy of EqpSch_Unoccupied created in the notebook.
S29 | – (new) | Heating availability schedule | Cell (added by nb) | rl_IsScheduledBy_Heating | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Heating | IFC DesignTransferView | schedule id | Value of last cell iterated | Room → IdealAirSystem | – | HVACTemplate:Zone:IdealLoadsAirSystem | Heating_Availability_Schedule_Name | – | id; prefix 'HtnSch_' | 'AlwaysOff' | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×81); HtnSch_AHU (×75) | None (×26); HtnSch_AHU (×23) | B09: HtnSch_AHU (×52); AlwaysOff (×13) ¦ B10: HtnSch_AHU (×12); AlwaysOff (×8) | B09: HtnSch_AHU (×52); AlwaysOff (×13) ¦ B10: HtnSch_AHU (×12); AlwaysOff (×8) | HtnSch_AHU: 07–18 h all year (baseline); always 1 (calibrated).
S30 | – (new) | Cooling availability schedule | Cell (added by nb) | rl_IsScheduledBy_Cooling | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Cooling | IFC DesignTransferView | schedule id | Value of last cell iterated | Room → IdealAirSystem | – | HVACTemplate:Zone:IdealLoadsAirSystem | Cooling_Availability_Schedule_Name | – | id; prefix 'ClnSch_' | 'AlwaysOff' | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×81); ClnSch_AHU (×75) | None (×26); ClnSch_AHU (×23) | B09: ClnSch_AHU (×52); AlwaysOff (×13) ¦ B10: ClnSch_AHU (×12); AlwaysOff (×8) | B09: ClnSch_AHU (×52); AlwaysOff (×13) ¦ B10: ClnSch_AHU (×12); AlwaysOff (×8) | ClnSch_AHU: 07–18 h from 16/4 to 14/10 (baseline); always 1 (calibrated).
S31 | – (new) | Ventilation (system) availability schedule | Cell (added by nb) | rl_IsScheduledBy_Ventilation | IfcSpace | Altro (B09) / Other (B10) | rl_IsScheduledBy_Ventilation | IFC DesignTransferView | schedule id | Value of last cell iterated | Room → IdealAirSystem | – | HVACTemplate:Zone:IdealLoadsAirSystem | System_Availability_Schedule_Name | – | id; prefix 'VntSch_' | 'AlwaysOff' | Yes | TopologicCellComplexToIDF (scripts/01_bim_to_bem.py) | None (×81); VntSch_AHU (×75) | None (×26); VntSch_AHU (×23) | B09: VntSch_AHU (×52); AlwaysOff (×13) ¦ B10: VntSch_AHU (×12); AlwaysOff (×8) | B09: VntSch_AHU (×52); AlwaysOff (×13) ¦ B10: VntSch_AHU (×12); AlwaysOff (×8) | System availability switches the whole ideal-loads system (heating, cooling and outdoor air).
S32 | – (new) | Storey | Cell | rl_HasLocation_tpBS | IfcSpace / IfcBuildingStorey | Altro (B09) / Other (B10) | rl_HasLocation_tpBS | Topologic JSON | id | Taken from zone dictionary | Room | story | – | – (HB story is not written to IDF) | – | none | 'noneStorey' | No | TopologicCellComplexToIDF | BuildingStorey_-595cm (×45); BuildingStorey_5cm (×42); BuildingStorey_1029cm (×35); BuildingStorey_517cm (×33) | BuildingStorey_-595cm (×21); BuildingStorey_5cm (×15); BuildingStorey_517cm (×12); BuildingStorey_1029cm (×1) | – | – | Also used to build zone ids before renaming (storey-clusterN).
S33 | – (new) | Space / zone identifier | Cell → zone CellComplex | UID → rl_HasLocation_tpZN | IfcSpace | Altro (B09) / Other (B10) | UID | Topologic JSON | id | Cells grouped by rl_HasLocation_tpZN (K-Means + adjacency rules) → CellComplex.ByCells | Room | identifier = zone UID ('zoneNN') | Zone | Name | – | none | 'debugZoneN' for unassigned cells (B09 nb) | Yes | TBIM.EnergyZones; HBRoom(tpZoneUID, faces, 0.01, 1) | 155 cells | 49 cells | B09: 65 zones ¦ B10: 20 zones | same
S34 | – (new) | Area / volume | Cell | pr_GrossArea, pr_NetVolume … (stored) / Cell.Area(), Cell.Volume() (computed) | IfcSpace | Qto_SpaceBaseQuantities | GrossFloorArea, NetVolume | Topologic geometry | cm² / cm³ | Used as weights for aggregations | Room | floor_area / volume (from geometry) | Zone | Floor_Area / Volume = autocalculate | m² / m³ | from geometry | – | Partial | Utils.TopologicZoneInheritSpaceData (Operation.py:4) | – | – | autocalculated by E+ | same | Stored BIM quantities are not used; E+ recomputes from surfaces.

## Map_Envelope
ID | Paper table | Paper property name | Topologic entity | Topologic key | IFC entity | IFC pset | IFC property | Read by workflow from | BIM unit | Cell → zone aggregation | Honeybee object | Honeybee attribute | EnergyPlus object | EnergyPlus field | E+ unit | Conversion BIM → E+ | Default if missing / 'Undefined' | In IDF? | Implementation | Value B09 (BIM) | Value B10 (BIM) | Value in IDF – baseline | Value in IDF – calibrated | Notes
E01 | T8 | – (surface classification) | Face | pr_TopologicalType (extVer / intVer / topHor / botHor / intHor) | – (derived) | – | – | Topologic JSON (set from CellComplex.Decompose if missing) | text | – | Face | type: 'VER'→Wall, 'HOR'→Floor, 'TOP'→RoofCeiling | BuildingSurface:Detailed | Surface_Type (Wall / Floor / Roof / Ceiling) | – | keyword | set by CellComplex.Decompose | Yes | HB.HBFacesByTopologicZone (Operation.py:999) | see Val_Constructions | see Val_Constructions | Wall / Floor / Roof / Ceiling | same | Interior HB Floor/RoofCeiling pairs become Floor/Ceiling after solve_adjacency.
E02 | T8 | Construction Name | Face | pr_WallTypeName (extVer, intVer) / pr_RoofTypeName (topHor) / pr_FloorTypeName (botHor, intHor) → HBConstructionName | IfcWallType / IfcSlabType / IfcRoofType | – | Name ('Family:Type'; part after ':') | Topologic JSON + IFC DesignTransferView | text | – | OpaqueConstruction | identifier / display_name | BuildingSurface:Detailed | Construction_Name | – | match by name; only if name ∈ HB opaque constructions | HB default ('Generic Interior Wall', 'Generic Interior Floor', 'Generic Ground Slab'); 'Generic Exterior Wall' → WL_POLIMI-LC_EW02; 'Generic Roof' → RF_POLIMI-LC_IH-E | Yes | TBIM.Faces_SetHBConstructionName; Eppy.IdfSetFaceConstructions | see Val_Constructions | see Val_Constructions | see Val_Constructions | same | Construction names are re-assigned with Eppy after the HB→IDF export.
E03 | T8 | – (layer set) | – | – | IfcWallType / IfcSlabType | IfcRelAssociatesMaterial | IfcMaterialLayerSet.MaterialLayers (order kept: outside → inside) | IFC DesignTransferView | – | – | OpaqueConstruction | materials (list, outside → inside) | Construction | Outside_Layer, Layer_2 … Layer_10 | – | 1:1 order | construction skipped if no layer has λ, ρ and c | Yes | HB.HBOpaqueConstructionsByIFCPaths (Operation.py:234); Eppy.IdfSetConstructionsAndMaterials | see Val_Layers | see Val_Layers | see Val_Layers | same | IfcRoofType has no layer set in either IFC → roof construction typed in the notebook (E14).
E04 | T8 | – (material name) | – | – | IfcMaterial | – | Name | IFC ReferenceView | text | – | EnergyMaterial | identifier = '{Name}-{thickness_m}' (',' → '-') | Material | Name | – | string | – | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same
E05 | T8 | – (layer thickness) | – | – | IfcMaterialLayer | – | LayerThickness | IFC DesignTransferView | cm | – | EnergyMaterial | thickness | Material | Thickness | m | ÷ 100 | 0 → 0.005 m | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same | Waterproofing membranes have LayerThickness 0 in IFC → 5 mm in E+.
E06 | T8 | – (thermal conductivity) | – | – | IfcMaterial | IfcMaterialProperties | ThermalConductivity | IFC ReferenceView | W/m·K | – | EnergyMaterial | conductivity | Material | Conductivity | W/m·K | round(·, 3) | material skipped | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same | Air cavities are written as massive Material with λ = 0.285 / 1.0 W/m·K and ρ = 1 kg/m³ (no Material:AirGap).
E07 | T8 | – (density) | – | – | IfcMaterial | IfcMaterialProperties | Density (not MassDensity) | IFC ReferenceView | kg/m³ | – | EnergyMaterial | density | Material | Density | kg/m³ | 1:1 | material skipped | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same | IFC carries two densities (Density, MassDensity) that differ, e.g. insulation 30 vs 80 kg/m³; the workflow uses 'Density'.
E08 | T8 | – (specific heat) | – | – | IfcMaterial | IfcMaterialProperties | SpecificHeatCapacity (any name containing 'HEAT') | IFC ReferenceView | J/kg·K | – | EnergyMaterial | specific_heat | Material | Specific_Heat | J/kg·K | int() (truncation) | material skipped | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same
E09 | T8 | – (emissivity) | – | – | IfcMaterial | IfcMaterialProperties | Emissivity | IFC ReferenceView | – | – | EnergyMaterial | thermal_absorptance | Material | Thermal_Absorptance | – | if ε > 0.05: round(ε, 2) else 0.7 | 0.9 | Yes | HB.HBOpaqueConstructionsByIFCPaths | see Val_Layers | see Val_Layers | see Val_Layers | same
E10 | T8 | – (solar absorptance) | – | – | – | – | – | notebook constant | – | – | EnergyMaterial | solar_absorptance | Material | Solar_Absorptance | – | constant | 0.7 | Partial | HB.HBOpaqueConstructionsByIFCPaths | 0.7 | 0.7 | 0.7 (all opaque materials) | same | IFC 'Analytical Properties.Absorptance' is not read by the active function.
E11 | T8 | – (visible absorptance) | – | – | – | – | – | notebook constant | – | – | EnergyMaterial | visible_absorptance | Material | Visible_Absorptance | – | constant | 0.7 | Partial | HB.HBOpaqueConstructionsByIFCPaths | 0.7 | 0.7 | 0.7 | same
E12 | T8 | – (roughness) | – | – | – | – | – | notebook constant | – | – | EnergyMaterial | roughness | Material | Roughness | – | constant | MediumRough | Partial | HB.HBOpaqueConstructionsByIFCPaths | MediumRough | MediumRough | MediumRough | same
E13 | T8 | Thermal Transmittance (wall / roof / ground floor / partitions) | – | – | IfcWallType / IfcSlabType | Analytical Properties | Heat Transfer Coefficient (U) / Thermal Resistance (R) | not read | W/m²K | – | OpaqueConstruction | u_value (derived from layers) | Construction | (none – E+ derives U from layers) | W/m²K | – | – | No | (legacy HB.HBOpaqueConstructionsByIFC reads R but is not called) | see Val_Constructions (computed) | see Val_Constructions (computed) | see Val_Constructions | same | Report U computed from the IDF layers (Val_Constructions), not stored IFC U-values.
E14 | T8 | Roof construction | Face | pr_RoofTypeName | IfcRoofType | – | Name (no material layers in IFC) | notebook constant | – | – | OpaqueConstruction | RF_POLIMI-LC_IH-E: Ghiaia 0.08 / Massetto 0.12 / Isolante rigido 0.08 / CLS 0.25 m | Construction + Material | all layer fields | SI | typed in scripts/01_bim_to_bem.py | – | Partial | scripts/01_bim_to_bem.py | RF_POLIMI-LC_IH-E, RF_POLIMI-LC_INH-E | RF_POLIMI-LC_IH-E | RF_POLIMI-LC_IH-E only | same | Faces typed RF_POLIMI-LC_INH-E (15 in B09) fall back to 'Generic Roof' → RF_POLIMI-LC_IH-E.
E15 | – (new) | Outside boundary condition | Face | UID (lists adiabaticFaceUIDs / groundFaceUIDs in nb) | – | – | – | HB + notebook constant | – | – | Face | boundary_condition (Outdoors / Ground / Surface via Room.solve_adjacency) | BuildingSurface:Detailed | Outside_Boundary_Condition (+ Outside_Boundary_Condition_Object) | – | 'Adiabatic' / 'Ground' forced by face UID | Outdoors | Yes | HBRoom.solve_adjacency(tol 0.01); TopologicCellComplexToIDF 'SURFACE CONDITIONS' | adiabatic: extVerFace13, 14, 140, 142, 143; ground: 17 faces | adiabatic: extVerFace8–14 | B09: Surface (×1190); Outdoors (×471); Ground (×63); Adiabatic (×5) ¦ B10: Surface (×260); Outdoors (×135); Ground (×15); Adiabatic (×7) | same | Faces of excluded cells (notUsefullCellUIDs) leave their neighbours exposed: interior partitions become 'Outdoors'.
E16 | – (new) | Surface geometry | Face | Face.ExternalBoundary vertices | IfcSpace boundaries (via TBIM) | – | – | Topologic geometry | cm | – | Face | geometry = Face3D(Point3D) | BuildingSurface:Detailed | Vertex_n_X/Y/Zcoordinate | m | ÷ 100 | – | Yes | HB.HBFacesByTopologicZone | – | – | GlobalGeometryRules: UpperLeftCorner, Counterclockwise, Relative | same
E17 | – (new) | Surface identifier | Face | UID | – | – | – | Topologic JSON | id | – | Face | identifier = '{faceUID}-{zoneUID}' | BuildingSurface:Detailed | Name | – | string | – | Yes | HB.HBFacesByTopologicZone | e.g. extVerFace62-zone27 | e.g. extVerFace0-zone12 | same pattern | same | Join key between TBIM faces and IDF surfaces.

## Map_Apertures
ID | Paper table | Paper property name | Topologic entity | Topologic key | IFC entity | IFC pset | IFC property | Read by workflow from | BIM unit | Cell → zone aggregation | Honeybee object | Honeybee attribute | EnergyPlus object | EnergyPlus field | E+ unit | Conversion BIM → E+ | Default if missing / 'Undefined' | In IDF? | Implementation | Value B09 (BIM) | Value B10 (BIM) | Value in IDF – baseline | Value in IDF – calibrated | Notes
A01 | T9 | – (aperture type) | Aperture (Face) | pr_TopologicalType (window / door / hole) | IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_TopologicalType | Topologic JSON | text | – | Aperture | (window and door → Aperture; hole → skipped) | FenestrationSurface:Detailed | Surface_Type = Window | – | keyword | – | Partial | HB.HBFacesByTopologicZone | door ×211, hole ×38 (no IfcWindow) | door ×67, hole ×16, window ×1 | B09: Window (×55) ¦ B10: Window (×25) | same | Doors are modelled as glazed HB Apertures; HB Door / E+ Door objects are never created (hbRoomDoors stays empty). Apertures are dropped on faces that are curtain walls or adiabatic: only 1 door (B09) and 3 doors + 1 window (B10) reach the IDF.
A02 | T9 | – (curtain wall) | Face | pr_WallTypeName contains 'CURTAIN' | IfcWall (type …CurtainWall / …CurtainWall150) | – | type Name | Topologic JSON | text | – | Aperture | identifier 'curtainWall-{faceUID}'; geometry = face scaled 0.9 × 0.9 about its centre (≈ 81 % of face area) | FenestrationSurface:Detailed | Name / vertices | m | linear scale 0.9 | – | Yes | HB.HBFacesByTopologicZone | 55 extVer curtain-wall faces (+47 intVer, no aperture) | WL_POLIMI-LC_CurtainWall faces (see Val_Glazing) | see Val_Glazing | same | Glazing fraction is fixed by the scale factor, not by pr_WindowGlazingAreaFraction (0.8).
A03 | T9 | Thermal Transmittance | Face (curtain wall) / Aperture | pr_WindowThermalTrasmittance / pr_ThermalTrasmittance | IfcWall (curtain) / IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_WindowThermalTrasmittance / pr_ThermalTrasmittance | IFC DesignTransferView | W/m²K | – | WindowConstruction (from_simple_parameters) | u_factor | WindowMaterial:SimpleGlazingSystem | UFactor | W/m²K | 1:1 | first construction in list / HB 'Generic Double Pane' | Yes | HB.HBWindowConstructionsByIFC (Operation.py:908; inline copy in B09 nb); Eppy.IdfSetWindowConstructions / IdfSetCurtainWallConstructions | 0.9 | 0.9 (NaN on 39 doors, 2 curtain walls) | 0.9 | 0.9 | Whole-window U; frame and glass U (A08, A09) are not used separately.
A04 | T9 | Solar Heat Gain Transmittance | Face / Aperture | pr_WindowSolarTrasmittance / pr_SolarTrasmittance | IfcWall / IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_WindowSolarTrasmittance / pr_SolarTrasmittance | IFC DesignTransferView | – | – | WindowConstruction | shgc | WindowMaterial:SimpleGlazingSystem | Solar_Heat_Gain_Coefficient | – | 1:1 | as above | Yes | as A03 | 0.67 | 0.67 | 0.67 | 0.67
A05 | T9 | Visible Light Transmittance | Face / Aperture | pr_WindowVisibleTrasmittance / pr_VisibleTrasmittance | IfcWall / IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_WindowVisibleTrasmittance / pr_VisibleTrasmittance | IFC DesignTransferView | – | – | WindowConstruction | vt | WindowMaterial:SimpleGlazingSystem | Visible_Transmittance | – | 1:1 | as above | Yes | as A03 | 0.8 (IFC); TBIM faces 0.8 ×103, 0.58 ×121 | 0.8 / 0.58 | B09: 0.8 ¦ B10: 0.8, 0.58 | same | B09: the TBIM has VT 0.58 on 121 curtain-wall faces but the B09 IFC only defines VT 0.8, so those panels (23 in the IDF) fall back to HB 'Generic Double Pane'.
A06 | – (new) | Glazing construction name | Face / Aperture | (built) | – | – | – | derived | text | – | WindowConstruction | identifier 'windowConstruction_U{U}_SHGC{g}_VT{vt}' / 'curtainWallWindowConstruction_…' | Construction (1 layer) + FenestrationSurface:Detailed | Name / Construction_Name | – | string | hbWindowConstructionNames[0] | Yes | Eppy.IdfSetConstructionsAndMaterials | see Val_Glazing | see Val_Glazing | see Val_Glazing | same
A07 | T9 | Glass Layers | Face / Aperture | pr_WindowGlassLayers / pr_GlassLayers | IfcWindow / IfcDoor / IfcWall | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_GlassLayers | not read | text | – | – | – | – | – | – | – | – | No | – | Double | Double | – | – | Simple glazing model: number of panes is implicit in U/SHGC.
A08 | T9 | Glass Thermal Transmittance | Face / Aperture | pr_WindowGlassTermalTrasmittance / pr_GlassTermalTrasmittance | IfcWindow / IfcDoor / IfcWall | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_GlassTermalTrasmittance | not read | W/m²K | – | – | – | – | – | – | – | – | No | – | 1.1 | 1.1 | – | – | Glass U (1.1) > whole-window U (0.9) with frame U 0.7: check consistency.
A09 | T9 | Frame Material / frame U | Face / Aperture | pr_WindowFrameMaterial, pr_WindowFrameThermalTrasmittance | IfcWindow / IfcDoor / IfcWall | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_FrameMaterial, pr_FrameThermalTrasmittance | not read | text / W/m²K | – | – | – | (WindowProperty:FrameAndDivider not generated) | – | – | – | – | No | – | Aluminium; 0.7 | Aluminium; 0.7 | – | –
A10 | T9 | Glazing Area Fraction | Face / Aperture | pr_WindowGlazingAreaFraction / pr_GlazingAreaFraction | IfcWindow / IfcDoor / IfcWall | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_GlazingAreaFraction | not read | – | – | – | – | – | – | – | – | – | No | – | 0.8 | 0.8 | – | – | See A02: curtain-wall glazing = 0.81 by geometry.
A11 | T9 | Width / Height | Aperture | pr_Width, pr_Heigth (sic) | IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_Width, pr_Heigth | not read (geometry used instead) | cm | – | Aperture | geometry from aperture face vertices | FenestrationSurface:Detailed | Vertex_n_X/Y/Zcoordinate | m | ÷ 100 | – | Partial | HB.HBFacesByTopologicZone | None | per aperture | – | – | Paper values (2.80 × 1.50 m) are not model values.
A12 | T9 | Wind Load Rating | Face / Aperture | pr_WindowWindLoadRating / pr_WindLoadRating | IfcWindow | Other (IfcWindow/IfcDoor) – Altro in B09 | pr_WindLoadRating | not read | class | – | – | – | – | – | – | – | – | No | – | A4 | A3 | – | –
A13 | – (new) | Aperture identifier / host | Aperture | UID, uuid, rl_HasLocation_inFC | IfcWindow / IfcDoor | Other (IfcWindow/IfcDoor) – Altro in B09 | UID | Topologic JSON | id | – | Aperture / Face | identifier '{UID}-{uuid}'; Face.add_apertures | FenestrationSurface:Detailed | Name / Building_Surface_Name | – | string | – | Yes | HB.HBFacesByTopologicZone | – | – | – | –
A14 | – (new) | External blinds | Aperture | (list fenestrationSurfaceWithBlinds in nb) | – | – | – | notebook constant | – | – | – | – | WindowMaterial:Blind + WindowShadingControl + Construction '…-withBlinds-…' | Slat width 0.30 m, separation 0.50 m, thickness 0.001 m, angle 90° (min 85, max 95), λ 160 W/m·K, beam/diffuse solar refl. 0.6, visible refl. 0.5, IR emissivity 0.9, blind-to-glass 0.30 m, side openings 0.5; Shading_Type ExteriorBlind, Control AlwaysOn, FixedSlatAngle | SI | constants | – | Partial | TopologicCellComplexToIDF 'BLINDS' | 11 curtain-wall surfaces | 3 curtain walls + 1 window | B09: 11 controls ¦ B10: 4 | same | Not derived from BIM; consider adding an IFC shading device property.

## Map_Model
ID | Topic | Topologic entity | Topologic key(s) | IFC entity | IFC detail | Source | Rule / value | Honeybee object | Honeybee attribute | EnergyPlus object | EnergyPlus field(s) | In IDF? | Implementation | Value B09 | Value B10 | Notes
M01 | Zoning: clustering | Cell | pr_IsOccupied, pr_IsHeated, pr_IsCooled, pr_OccupancyDensityOperation | IfcSpace | → IfcZone (exported) | Topologic JSON | K-Means (n_clusters = 6, StandardScaler, random_state = 14); single-cell zones for LectureHall, Research Lab, GeneralStorage; stairs/elevators → adjacent corridor; HorizontalInfrastructure → corridor/stair, then restroom; split by adjacency; excluded cells notUsefullCellUIDs | Room | one Room per zone CellComplex | Zone | Name, Multiplier = 1, Volume/Area autocalculate | Yes | TBIM.Cells_ClusterizeIntoEnergyZones (Operation.py:1517; inline copy in B09 nb) | B09: 65 zones (incl. 12 'debugZone') | B10: 20 zones | Excluded B09: Cell59, 115–125, 153; B10: Cell3, 22–25, 29.
M02 | Zoning: data inheritance | Zone CellComplex | see Map_Spaces 'Cell → zone aggregation' | – | – | Topologic | OR / area-weighted / occupant-weighted / min / max / prevalent | Room | – | People, Lights, … | – | Yes | Utils.TopologicZoneInheritSpaceData (Operation.py:4) |  |  | Bug: schedules and pr_MechanicalVentilationRate take the last cell's value.
M03 | Geometry units | Vertex | X, Y, Z | – | – | Topologic | cm → m (÷ 100) | Face3D / Point3D | – | BuildingSurface:Detailed | vertices | Yes | HB.HBFacesByTopologicZone
M04 | Room creation | Zone CellComplex + Faces | – | – | – | Topologic | HBRoom(identifier, faces, tolerance = 0.01 m, angle tolerance = 1°); Room.solve_adjacency(0.01) | Room | identifier, faces, story | Zone + BuildingSurface:Detailed | – | Yes | TopologicCellComplexToIDF
M05 | Context shading | Face (BRep) | – | – | – | BRep files *_Shades-Balconies / -ContextBuildings / -AdjacentBuildings.brep | cm → m; Vegetation BRep not used | Shade (is_detached = True) | identifier 'shade{j}-{i}' | Shading:Building:Detailed | Name, vertices | Yes | HB.HBShadesByTopologicBRepPaths | 88 shades | 79 shades | Shades are opaque, no transmittance schedule.
M06 | HB program (base loads) | – | – | – | – | HB library | honeybee_energy.lib.programtypes.office_program, then People/Lights/Equipment/OA overwritten by Eppy | Room | properties.energy.program_type | People, Lights, ElectricEquipment, ZoneInfiltration, DesignSpecification:OutdoorAir | names 'Generic Office …' | Partial | HB.HBRoomSetSetpointSchedules |  |  | Activity 'Seated Adult Activity', infiltration schedule 'Generic Office Infiltration' stay from the office program.
M07 | Ideal loads HVAC | – | – | – | – | HB default | add_default_ideal_air() | Room | properties.energy.hvac (IdealAirSystem) | HVACTemplate:Zone:IdealLoadsAirSystem | Max heating SAT 50 °C; min cooling SAT 13 °C; heating limit LimitCapacity (autosize); cooling limit LimitFlowRateAndCapacity (autosize); economizer DifferentialDryBulb; heat recovery None; DCV None | Partial | HB.HBRoomSetSetpointSchedules |  |  | No AHU capacity caps (paper: 7,200 / 11,000 m³/h).
M08 | Thermostat | – | – | – | – | HB constant | Setpoint('Room Setpoint', heating 20 °C, cooling 26 °C) | Room | properties.energy.setpoint | HVACTemplate:Thermostat + Schedule:Constant | Heating/Cooling_Setpoint_Schedule_Name | Partial | HB.HBRoomSetSetpointSchedules | baseline 20/26 °C | calibrated: see S19/S22
M09 | Infiltration | – | – | – | – | notebook constant | infiltrationFlowRateDict['TightBuilding'] = 0.0001 m³/s per m² exterior surface | Room | infiltration (office program) | ZoneInfiltration:DesignFlowRate | Design_Flow_Rate_Calculation_Method = Flow/ExteriorArea; Flow_Rate_per_Exterior_Surface_Area = 0.0001; coefficients 1/0/0/0; schedule 'Generic Office Infiltration' | Partial | TopologicCellComplexToIDF 'CONSTRUCTION' | 0.0001 | 0.0001 | Options in nb: PassiveHouse 7.1e-5, Tight 1e-4, Average 3e-4, Leaky 6e-4.
M10 | Service hot water | – | – | – | – | HB constant | ServiceHotWater('Office Hot Water', 0.1 L/h·m², 'Office room dayschedule' 9–17 h) | Room | service_hot_water | WaterUse:Equipment | Peak_Flow_Rate, Flow_Rate_Fraction_Schedule_Name | Partial | HB.HBRoomSetSetpointSchedules |  |  | Not BIM-derived; outputs not reported in the paper.
M11 | Schedules | – | – | – | – | _schedules/*.json (HB ScheduleRuleset dicts) | rules → 'Through: m/d' / 'For: <weekday ¦ Weekdays ¦ AllDays>' / 'Until: hh:00', value clipped to type limits | ScheduleRuleset (dict) | identifier (prefixed) | Schedule:Compact + ScheduleTypeLimits | Name, Schedule_Type_Limits_Name, Field_n | Yes | HB.*ScheduleRulesetDictsByJSONPath; Eppy.IdfScheduleCompactByHBScheduleRulesetDict (Operation.py:1183) |  |  | See Val_Schedules. Prefixes: OccSch_, EqpSch_, LghSch_, HtnSch_, ClnSch_, VntSch_. Plus 'AlwaysOff'.
M12 | Building | – | – | – | – | notebook constant | buildingName, northAxis = 45°, terrain = 'City' | Model | identifier | Building | Name, North_Axis, Terrain, Solar_Distribution = FullExterior (overrides HB value) | Yes | TopologicCellComplexToIDF | edificio09, 45°, City | edificio10, 45°, City
M13 | Simulation control | – | – | – | – | HB.HBDefaultSimulationParameter | zone sizing Yes, system/plant sizing No, sizing periods No, run periods Yes | SimulationParameter | simulation_control | SimulationControl | all fields | Yes | Operation.py:468
M14 | Timestep | – | – | – | – | HB.HBDefaultSimulationParameter | 6 per hour (nb attempt to set 4 has no effect) | SimulationParameter | timestep | Timestep | Number_of_Timesteps_per_Hour | Yes | Operation.py:531 | baseline 6, calibrated 4 | baseline 6, calibrated 4
M15 | Run period | – | – | – | – | HB default + Eppy at run time | IDF: 1/1–31/12/2017, start Monday; overwritten to 2024 by Eppy.EnergyPlus_RunSimulation | RunPeriod | start/end date | RunPeriod | Begin/End Month/Day/Year | Yes | Operation.py:1132 |  |  | Paper: monitoring period 1/2/2024–31/1/2025.
M16 | Daylight saving / holidays | – | – | – | – | HB default | DST 12/3–5/11; holidays 1/1 and 4/7 | RunPeriod | daylight_saving_time, holidays | RunPeriodControl:DaylightSavingTime / :SpecialDays | Start/End Date | Yes | Operation.py:482 |  |  | US defaults (4 July); Italian DST is last Sun of March → last Sun of October.
M17 | Shadow calculation | – | – | – | – | HB.HBDefaultSimulationParameter | PolygonClipping, Periodic, every 30 days, max 15 000 figures | ShadowCalculation | – | ShadowCalculation | all fields | Yes | Operation.py:507
M18 | Sizing | – | – | – | – | HB default + DDY | heating factor 1.25, cooling factor 1.15; design days from ITA_LM_Grigna.Settentrion.160700_TMYx.ddy (99.6 % htg DB, 0.4 % clg DP) | SizingParameter | – | Sizing:Parameters + SizingPeriod:DesignDay | – | Yes | Operation.py:516; nb 'add_from_ddy_996_004'
M19 | Weather | – | – | – | – | EPW | data/weather/Lecco_IT-hour.epw | – | – | (simulation input) | – | Yes | Eppy.EnergyPlus_RunSimulation
M20 | Outputs | – | – | – | – | Eppy.DigitManOutputVariables + nb | Zone Ideal Loads Zone Total Heating/Cooling Energy, Zone Electric Equipment Electricity Energy, Zone Lights Electricity Energy, Zone People Occupant Count, Zone Mean Air / Air / Mean Radiant / Operative Temperature | SimulationOutput | outputs | Output:Variable | Variable_Name, Reporting_Frequency = Hourly | Yes | Eppy.IdfSetOutputVariables |  |  | Calibration uses ZONE18 Mean Radiant Temperature (B10).

## Val_SpaceTypes
Building | pr_OccupancyType | N cells | pr_OccupancyType_Number | pr_IsOccupied | pr_IsHeated | pr_IsCooled | pr_IsMechanicallyVentilated | pr_IsNaturallyVentilated | pr_ArtificialLighting | pr_OccupancyDensityOperation | pr_OccupancyDensitySafety | pr_LightingPowerDensity | pr_EquipmentPowerDensity | pr_Illuminance | pr_MechanicalVentilationRate | pr_MechanicalVentilationRatePerPerson | pr_MechanicalVentilationRatePerVolume | pr_SpaceTemperatureSummerMax | pr_SpaceTemperatureSummerMin | pr_SpaceTemperatureWinterMax | pr_SpaceTemperatureWinterMin | pr_HumidityMax | pr_HumidityMin | pr_SpaceWindLoadRating | rl_IsScheduledBy_Occupancy (IFC) | rl_IsScheduledBy_Lighting (IFC) | rl_IsScheduledBy_Equipment (IFC) | rl_IsScheduledBy_Heating (IFC) | rl_IsScheduledBy_Cooling (IFC) | rl_IsScheduledBy_Ventilation (IFC)
B09 | CommerceActivitySpaces:OfficeSpaces | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 0.12 | 0.4 | 7 | Undefined | 500 | 0.68599 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×1) | LghSch_Costant (×1) | EqpSch_Costant (×1) | HtnSch_AHU (×1) | ClnSch_AHU (×1) | VntSch_AHU (×1)
B09 | EducationandTrainingSpaces:LectureHall(FixedSeats) | 19 | 5 | 1 | 1 | 1 | 1 | 0 | 1 | 0.6 | 1.2 | 6 | Undefined | 300 | 0.33794–5.80349 (17 distinct) | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | A4 (×18); Undefined (×1) | OccSch_B0.1 (×2); OccSch_B0.7 (×1); OccSch_B0.6 (×1); OccSch_Unoccupied (×1); OccSch_B0.5 (×1); OccSch_B1.3 (×1); OccSch_B0.4 (×1); OccSch_B0.3 (×1); OccSch_B0.2 (×1); OccSch_B1.5 (×1); OccSch_B1.4 (×1); OccSch_B1.2 (×1); OccSch_B1.1 (×1); OccSch_B2.4 (×1); OccSch_B2.3 (×1); OccSch_B2.6 (×1); OccSch_B2.5 (×1); OccSch_B2.2 (×1) | LghSch_Costant;LghSch_B0.1 (×2); LghSch_Costant;LghSch_B0.7 (×1); LghSch_Costant;LghSch_B0.6 (×1); LghSch_Costant (×1); LghSch_Costant;LghSch_B0.5 (×1); LghSch_Costant;LghSch_B1.3 (×1); LghSch_Costant;LghSch_B0.4 (×1); LghSch_Costant;LghSch_B0.3 (×1); LghSch_Costant;LghSch_B0.2 (×1); LghSch_Costant;LghSch_B1.5 (×1); LghSch_Costant;LghSch_B1.4 (×1); LghSch_Costant;LghSch_B1.2 (×1); LghSch_Costant;LghSch_B1.1 (×1); LghSch_Costant;LghSch_B2.4 (×1); LghSch_Costant;LghSch_B2.3 (×1); LghSch_Costant;LghSch_B2.6 (×1); LghSch_Costant;LghSch_B2.5 (×1); LghSch_Costant;LghSch_B2.2 (×1) | EqpSch_Costant;EqpSch_B0.1 (×2); EqpSch_Costant;EqpSch_B0.7 (×1); EqpSch_Costant;EqpSch_B0.6 (×1); EqpSch_Costant (×1); EqpSch_Costant;EqpSch_B0.5 (×1); EqpSch_Costant;EqpSch_B1.3 (×1); EqpSch_Costant;EqpSch_B0.4 (×1); EqpSch_Costant;EqpSch_B0.3 (×1); EqpSch_Costant;EqpSch_B0.2 (×1); EqpSch_Costant;EqpSch_B1.5 (×1); EqpSch_Costant;EqpSch_B1.4 (×1); EqpSch_Costant;EqpSch_B1.2 (×1); EqpSch_Costant;EqpSch_B1.1 (×1); EqpSch_Costant;EqpSch_B2.4 (×1); EqpSch_Costant;EqpSch_B2.3 (×1); EqpSch_Costant;EqpSch_B2.6 (×1); EqpSch_Costant;EqpSch_B2.5 (×1); EqpSch_Costant;EqpSch_B2.2 (×1) | HtnSch_AHU (×19) | ClnSch_AHU (×19) | VntSch_AHU (×19)
B09 | EducationandTrainingSpaces:Research/Non-ClassClassLaboratory | 23 | 6 | 1 | 1 | 1 | 1 | 0 | 1 | 0.3 | 0.4 | 6 | Undefined | 300 | 1.47905–1.90732 (23 distinct) | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | A4 | OccSch_Unoccupied (×23) | LghSch_Costant (×23) | EqpSch_Costant (×23) | HtnSch_AHU (×23) | ClnSch_AHU (×23) | VntSch_AHU (×23)
B09 | EducationandTrainingSpaces:StudyRoom | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 1 | 0.6 | 1.2 | 6 | Undefined | 300 | 3.73838 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×1) | LghSch_Costant (×1) | EqpSch_Costant (×1) | HtnSch_AHU (×1) | ClnSch_AHU (×1) | VntSch_AHU (×1)
B09 | FacilityServiceSpaces:Corridor | 8 | 13 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×8) | LghSch_Unoccupied (×7); LghSch_Costant (×1) | EqpSch_Unoccupied (×7); EqpSch_Costant (×1) | HtnSch_AHU (×5); None (×3) | ClnSch_AHU (×5); None (×3) | VntSch_AHU (×5); None (×3)
B09 | FacilityServiceSpaces:ElevatorShaft | 12 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 1 | 0 | 1 | Undefined | Undefined | Undefined | Undefined | 70 | 40 | Undefined | None (×12) | None (×12) | None (×12) | None (×12) | None (×12) | None (×12)
B09 | FacilityServiceSpaces:HorizontalInfrastructure/ServiceSpaceNon-Occupied | 56 | 12 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0–1332.16 (16 distinct) | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | None (×27); A4 (×17); Undefined (×12) | None (×55); OccSch_Unoccupied (×1) | None (×55); LghSch_Costant (×1) | None (×55); EqpSch_Costant (×1) | None (×51); HtnSch_AHU (×5) | None (×51); ClnSch_AHU (×5) | None (×51); VntSch_AHU (×5)
B09 | FacilityServiceSpaces:Restroom | 12 | 11 | 0 | 1 | 1 | 1 | 0 | 1 | Undefined | 0 | 6 | Undefined | Undefined | 8 | 0 | 8 | 26 | 23 | 23.5 | 18 | Undefined | Undefined | Undefined | OccSch_Unoccupied (×12) | LghSch_Costant (×12) | EqpSch_Costant (×12) | HtnSch_AHU (×9); None (×3) | ClnSch_AHU (×9); None (×3) | VntSch_AHU (×9); None (×3)
B09 | FacilityServiceSpaces:Stairway | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | Undefined | 150 | 1 | 0 | 1 | Undefined | Undefined | Undefined | Undefined | 70 | 40 | Undefined (×7); None (×2) | OccSch_Unoccupied (×7); None (×2) | LghSch_Unoccupied (×7); None (×2) | EqpSch_Unoccupied (×7); None (×2) | HtnSch_AHU (×7); None (×2) | ClnSch_AHU (×7); None (×2) | VntSch_AHU (×7); None (×2)
B09 | FacilityServiceSpaces:UtilityEquipmentRoom | 13 | 10 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined (×12); A4 (×1) | OccSch_Unoccupied (×12); None (×1) | LghSch_Costant (×12); None (×1) | EqpSch_Costant (×12); None (×1) | None (×9); HtnSch_AHU (×4) | None (×9); ClnSch_AHU (×4) | None (×9); VntSch_AHU (×4)
B09 | StorageSpaces:GeneralStorageSpace | 1 | 20 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 200 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×1) | LghSch_Costant (×1) | EqpSch_Costant (×1) | HtnSch_AHU (×1) | ClnSch_AHU (×1) | VntSch_AHU (×1)
B10 | EducationandTrainingSpaces:LectureHall(FixedSeats) | 4 | 5 | 1 | 1 | 1 | 1 | 0 | 1 | 0.6 | 1.2 | 6 | Undefined | 300 | 1.44286 / 1.56475 / 2.97108 / 3.3027 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | A4 (×3); Undefined (×1) | OccSch_A1.3 (×1); OccSch_A1.2 (×1); OccSch_A1.1 (×1); OccSch_A0.1/A0.2 (×1) | LghSch_A1.3;LghSch_Costant (×1); LghSch_A1.2;LghSch_Costant (×1); LghSch_A1.1;LghSch_Costant (×1); LghSch_A0.1/A0.2;LghSch_Costant (×1) | EqpSch_A1.3;EqpSch_Costant (×1); EqpSch_A1.2;EqpSch_Costant (×1); EqpSch_A1.1;EqpSch_Costant (×1); EqpSch_A0.1/A0.2;EqpSch_Costant (×1) | HtnSch_AHU (×4) | ClnSch_AHU (×4) | VntSch_AHU (×4)
B10 | EducationandTrainingSpaces:Research/Non-ClassClassLaboratory | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 1 | 0.3 | 0.4 | 6 | Undefined | 300 | 1.83147 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | A4 | OccSch_Unoccupied (×1) | LghSch_Unoccupied (×1) | EqpSch_Unoccupied (×1) | HtnSch_AHU (×1) | ClnSch_AHU (×1) | VntSch_AHU (×1)
B10 | FacilityServiceSpaces:Corridor | 8 | 13 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined (×7); None (×1) | OccSch_Unoccupied (×7); None (×1) | LghSch_Unoccupied (×5); LghSch_Costant (×2); None (×1) | EqpSch_Unoccupied (×5); EqpSch_Costant (×2); None (×1) | HtnSch_AHU (×4); None (×4) | ClnSch_AHU (×4); None (×4) | VntSch_AHU (×4); None (×4)
B10 | FacilityServiceSpaces:ElevatorShaft | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 1 | 0 | 1 | Undefined | Undefined | Undefined | Undefined | 70 | 40 | Undefined | None (×3); OccSch_Unoccupied (×2) | None (×4); LghSch_Costant (×1) | None (×4); EqpSch_Costant (×1) | None (×5) | None (×5) | None (×5)
B10 | FacilityServiceSpaces:HorizontalInfrastructure/ServiceSpaceNon-Occupied | 8 | 12 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | None | None (×7); OccSch_Unoccupied (×1) | None (×7); LghSch_Costant (×1) | None (×7); EqpSch_Costant (×1) | None (×8) | None (×8) | None (×8)
B10 | FacilityServiceSpaces:Restroom | 7 | 11 | 0 | 1 | 1 | 1 | 0 | 1 | Undefined | 0 | 6 | Undefined | Undefined | 8 | 0 | 8 | 26 | 23 | 23.5 | 18 | Undefined | Undefined | Undefined | OccSch_Unoccupied (×7) | LghSch_Costant (×7) | EqpSch_Costant (×5); EqpSch_Unoccupied (×2) | HtnSch_AHU (×7) | ClnSch_AHU (×7) | VntSch_AHU (×7)
B10 | FacilityServiceSpaces:Stairway | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | Undefined | 150 | 1 | 0 | 1 | Undefined | Undefined | Undefined | Undefined | 70 | 40 | Undefined (×4); None (×1) | OccSch_Unoccupied (×4); None (×1) | LghSch_Unoccupied (×4); None (×1) | EqpSch_Unoccupied (×3); None (×1); EqpSch_Costant (×1) | HtnSch_AHU (×4); None (×1) | ClnSch_AHU (×4); None (×1) | VntSch_AHU (×4); None (×1)
B10 | FacilityServiceSpaces:UtilityEquipmentRoom | 3 | 10 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 300 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×3) | LghSch_Unoccupied (×2); LghSch_Costant (×1) | EqpSch_Costant (×2); EqpSch_Unoccupied (×1) | None (×2); HtnSch_AHU (×1) | None (×2); ClnSch_AHU (×1) | None (×2); VntSch_AHU (×1)
B10 | ParkingSpaces:InteriorParkingSpaces | 3 | 15 | 0 | 0 | 0 | 0 | 1 | 1 | Undefined | 0.01 | 6 | 0 | 150 | Undefined | 0 | 0 | Undefined | Undefined | Undefined | Undefined | Undefined | Undefined | Undefined | OccSch_Unoccupied (×2); OccSch_A0.1/A0.2 (×1) | LghSch_Unoccupied (×2); LghSch_Costant (×1) | EqpSch_Costant (×3) | None (×3) | None (×3) | None (×3)
B10 | ProtectiveSpaces:EntryPorch | 1 | 16 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 6 | Undefined | 200 | 1 | 0 | 1 | Undefined | Undefined | Undefined | Undefined | Undefined | Undefined | Undefined | None (×1) | None (×1) | None (×1) | None (×1) | None (×1) | None (×1)
B10 | ServiceActivitySpaces:SnackBar | 1 | 18 | 1 | 1 | 1 | 1 | 0 | 1 | 0.8 | 0.7 | 6 | Undefined | 500 | 4.81128 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | Undefined | OccSch_Unoccupied (×1) | LghSch_Costant (×1) | EqpSch_Unoccupied (×1) | HtnSch_AHU (×1) | ClnSch_AHU (×1) | VntSch_AHU (×1)
B10 | StorageSpaces:GeneralStorageSpace | 3 | 20 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 6 | Undefined | 200 | 0 | 7 | 0 | 26 | 23 | 23.5 | 18 | 70 | 40 | None (×2); Undefined (×1) | OccSch_Unoccupied (×3) | LghSch_Unoccupied (×2); LghSch_Costant (×1) | EqpSch_Costant (×3) | None (×2); HtnSch_AHU (×1) | None (×2); ClnSch_AHU (×1) | None (×2); VntSch_AHU (×1)
Note on A1: Values exactly as stored in the TBIM (Topologic JSON) cell dictionaries, grouped by occupancy type. 'Undefined' is replaced by the defaults in Map_Spaces column R. Schedule columns come from IfcSpace psets (Altro/Other); 'None' = property missing → default schedule. Multi-valued numbers are shown as 'min–max (n distinct)'.

## Val_Zones
Building | Zone (E+ Zone.Name) | People/Area (person/m²) | Occupancy schedule | Lights (W/m²) | Lighting schedule – baseline | Equipment (W/m²) – baseline | Equipment (W/m²) – calibrated | Equipment schedule | OA per person (m³/s·p) | OA per person (L/s·p) | OA per floor area (m³/s·m²) | OA per floor area (L/s·m²) | OA method | System availability | Heating availability | Cooling availability | Dehumidification setpoint (%) | Humidification setpoint (%) | Thermostat heating schedule | Thermostat cooling schedule | Infiltration (m³/s per m² ext.) | N opaque surfaces | N fenestration surfaces
B09 | debugZone0 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone1 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone10 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017691 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone11 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone2 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 0
B09 | debugZone3 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone4 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.001663 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone5 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0014836 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone6 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.00186 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 0
B09 | debugZone7 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018059 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 9 | 0
B09 | debugZone8 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017792 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | debugZone9 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017518 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | zone00 | 0 | OccSch_Unoccupied | 0 | LghSch_Unoccupied | 0 | 0 | EqpSch_Unoccupied | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 100 | 0 | Generic room Heating | Generic room Cooling | 0.0001 | 55 | 0
B09 | zone01 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 18 | 0
B09 | zone02 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0.008 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 52 | 0
B09 | zone03 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0.001 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | zone04 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0.001 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 187 | 2
B09 | zone05 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 0
B09 | zone06 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 40 | 0
B09 | zone07 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 2 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 185 | 10
B09 | zone08 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 2 | AlwaysOff | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 40 | 0
B09 | zone09 | 0.6 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0037384 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 1
B09 | zone10 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0.001 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 186 | 8
B09 | zone11 | 0.12 | OccSch_Unoccupied | 7 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.00068599 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 11 | 1
B09 | zone12-0 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 21 | 0
B09 | zone12-1 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 0
B09 | zone12-2 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 0
B09 | zone13 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 59 | 0
B09 | zone14 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 234 | 12
B09 | zone15 | 0.6 | OccSch_B0.1 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0052642 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B09 | zone16 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018633 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 0
B09 | zone17 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017926 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 0
B09 | zone18 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017618 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 15 | 0
B09 | zone19 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0016851 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 0
B09 | zone20 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.001479 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 7 | 0
B09 | zone21 | 0.6 | OccSch_B2.3 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.00033794 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone22 | 0.6 | OccSch_B2.4 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0033067 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B09 | zone23 | 0.6 | OccSch_B2.6 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0044077 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B09 | zone24 | 0.6 | OccSch_B2.5 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0042903 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone25 | 0.6 | OccSch_B2.2 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0053662 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone26 | 0.6 | OccSch_B0.1 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0042743 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone27 | 0.6 | OccSch_B0.7 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0058035 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone28 | 0.6 | OccSch_B0.6 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.005481 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 11 | 1
B09 | zone29 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B09 | zone30 | 0.6 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0021208 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 1
B09 | zone31 | 0.6 | OccSch_B0.5 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0036741 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B09 | zone32 | 0.6 | OccSch_B1.3 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0029384 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 26 | 3
B09 | zone33 | 0.6 | OccSch_B0.4 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0045058 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 19 | 1
B09 | zone34 | 0.6 | OccSch_B0.3 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0053662 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 1
B09 | zone35 | 0.6 | OccSch_B0.2 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0043402 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B09 | zone36 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018018 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 21 | 0
B09 | zone37 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018329 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 11 | 0
B09 | zone38 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017161 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 11 | 0
B09 | zone39 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017668 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 22 | 0
B09 | zone40 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0019073 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 10 | 0
B09 | zone41 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017542 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 0
B09 | zone42 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018912 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 27 | 0
B09 | zone43 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017769 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 0
B09 | zone44 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0016995 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 15 | 0
B09 | zone45 | 0.6 | OccSch_B1.5 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0036731 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 12 | 1
B09 | zone46 | 0.6 | OccSch_B1.4 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0042903 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 1
B09 | zone47 | 0.6 | OccSch_B1.2 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.003049 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 1
B09 | zone48 | 0.6 | OccSch_B1.1 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0055209 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 15 | 1
B09 | zone49 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0018737 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 0
B09 | zone50 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0.007 |  | 0.0017667 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 14 | 0
B10 | zone00 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0.008 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 100 | 0 | Generic room Heating | Generic room Cooling | 0.0001 | 18 | 0
B10 | zone01 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0.001 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 20 | 0
B10 | zone02 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 35 | 0
B10 | zone03 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 0
B10 | zone04 | 0 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 24 | 0
B10 | zone05 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0.001 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 7 | 1
B10 | zone06 | 0 | OccSch_A0.1/A0.2 | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 100 | 0 | Generic room Heating | Generic room Cooling | 0.0001 | 9 | 0
B10 | zone07 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 33 | 0
B10 | zone08 | 0 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | 0 | EqpSch_Unoccupied | 0 |  | 0.001 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 66 | 4
B10 | zone09 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 0 | EqpSch_Unoccupied | 0 |  | 0.008 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 31 | 0
B10 | zone10 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0.001 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 15 | 0
B10 | zone11 | 0 | OccSch_Unoccupied | 6 | AlwaysOff | 0 | 0 | AlwaysOff | 0 |  | 0 |  | Maximum | AlwaysOff | AlwaysOff | AlwaysOff | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 68 | 6
B10 | zone12 | 0.8 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 0 | EqpSch_Unoccupied | 0.007 |  | 0.0048113 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 9 | 3
B10 | zone13 | 0 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | 0 | EqpSch_Unoccupied | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 12 | 0
B10 | zone14 | 0.3 | OccSch_Unoccupied | 6 | LghSch_Unoccupied | 0 | 0 | EqpSch_Unoccupied | 0.007 |  | 0.0018315 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 13 | 1
B10 | zone15 | 0.6 | OccSch_A1.2 | 6 | LghSch_A1.2 | 0 | 10 | EqpSch_A1.2 | 0.007 |  | 0.0033027 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 8 | 1
B10 | zone16 | 0.6 | OccSch_A1.1 | 6 | LghSch_A1.1 | 0 | 10 | EqpSch_A1.1 | 0.007 |  | 0.0014429 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 7 | 3
B10 | zone17 | 0 | OccSch_Unoccupied | 6 | LghSch_Costant | 0 | 2 | EqpSch_Costant | 0 |  | 0 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 6 | 0
B10 | zone18 | 0.6 | OccSch_A1.3 | 6 | LghSch_A1.3 | 0 | 10 | EqpSch_A1.3 | 0.007 |  | 0.0029711 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 17 | 2
B10 | zone19 | 0.6 | OccSch_A0.1/A0.2 | 6 | LghSch_A0.1/A0.2 | 0 | 10 | EqpSch_A0.1/A0.2 | 0.007 |  | 0.0015647 |  | Maximum | VntSch_AHU | HtnSch_AHU | ClnSch_AHU | 70 | 40 | Generic room Heating | Generic room Cooling | 0.0001 | 11 | 4
Note on G1: Baseline IDF = direct workflow output.
Note on H1: Calibrated IDF (manual edit during calibration).
Note on K1: Formula: m³/s × 1000.
Note on M1: Formula: m³/s × 1000.
Note on T1: Baseline: Schedule:Constant 20 °C. Calibrated: Schedule:Compact (see Map_Spaces S22).

## Val_Constructions
Building | Construction | Category | Source | IFC elements with this type | N layers | Total thickness (m) | Rsi (m²K/W) | Rse (m²K/W) | R layers (m²K/W) | U (W/m²K) | N surfaces in IDF | Surface types | Outdoors | Ground | Adiabatic | Surface (interzone)
B09 | Generic Interior Wall | Internal partition | HB default (no BIM match) | 0 | 3 |  | 0.13 | 0.13 |  |  | 94 | Wall (×94) | 0 | 0 | 0 | 94
B09 | Generic Interior Floor | Internal floor | HB default (no BIM match) | 0 | 3 |  | 0.1 | 0.1 |  |  | 360 | Wall (×225); Floor (×135) | 0 | 0 | 0 | 360
B09 | Generic Ground Slab | Ground floor | HB default (no BIM match) | 0 | 2 |  | 0.17 | 0 |  |  | 1 | Floor (×1) | 0 | 1 | 0 | 0
B09 | WL_POLIMI-LC_EW04 | External wall | IFC IfcMaterialLayerSet | 14 | 7 |  | 0.13 | 0.04 |  |  | 11 | Wall (×11) | 11 | 0 | 0 | 0
B09 | WL_POLIMI-LC_EW01 | External wall | IFC IfcMaterialLayerSet | 3 | 8 |  | 0.13 | 0.04 |  |  | 3 | Wall (×3) | 2 | 0 | 1 | 0
B09 | WL_POLIMI-LC_EW03 | External wall | IFC IfcMaterialLayerSet | 67 | 9 |  | 0.13 | 0.04 |  |  | 13 | Wall (×13) | 13 | 0 | 0 | 0
B09 | WL_POLIMI-LC_EW05 | External wall | IFC IfcMaterialLayerSet | 34 | 9 |  | 0.13 | 0.04 |  |  | 36 | Wall (×36) | 34 | 0 | 0 | 2
B09 | WL_POLIMI-LC_EW02 | External wall | IFC IfcMaterialLayerSet | 9 | 8 |  | 0.13 | 0.04 |  |  | 156 | Wall (×156) | 147 | 5 | 4 | 0
B09 | WL_POLIMI-LC_FC300-2 | External wall | IFC IfcMaterialLayerSet | 69 | 5 |  | 0.13 | 0.04 |  |  | 54 | Wall (×54) | 36 | 12 | 0 | 6
B09 | WL_POLIMI-LC_FC300-3 | External wall | IFC IfcMaterialLayerSet | 11 | 8 |  | 0.13 | 0.04 |  |  | 21 | Wall (×21) | 1 | 0 | 0 | 20
B09 | WL_POLIMI-LC_IW02 | Internal partition | IFC IfcMaterialLayerSet | 202 | 7 |  | 0.13 | 0.13 |  |  | 448 | Wall (×448) | 2 | 0 | 0 | 446
B09 | WL_POLIMI-LC_IW03 | Internal partition | IFC IfcMaterialLayerSet | 195 | 3 |  | 0.13 | 0.13 |  |  | 255 | Wall (×255) | 135 | 0 | 0 | 120
B09 | WL_POLIMI-LC_IW04 | Internal partition | IFC IfcMaterialLayerSet | 25 | 8 |  | 0.13 | 0.13 |  |  | 58 | Wall (×58) | 0 | 0 | 0 | 58
B09 | WL_POLIMI-LC_IW05_Toilet | Internal partition | IFC IfcMaterialLayerSet | 34 | 9 |  | 0.13 | 0.13 |  |  | 52 | Wall (×52) | 16 | 0 | 0 | 36
B09 | WL_POLIMI-LC_IW06_Toilet | Internal partition | IFC IfcMaterialLayerSet | 21 | 5 |  | 0.13 | 0.13 |  |  | 21 | Wall (×21) | 21 | 0 | 0 | 0
B09 | FL_POLIMI-LC_GroundFloor | Ground floor | IFC IfcMaterialLayerSet | 47 | 7 |  | 0.17 | 0 |  |  | 46 | Floor (×46) | 1 | 45 | 0 | 0
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | Internal floor | IFC IfcMaterialLayerSet | 24 | 5 |  | 0.1 | 0.1 |  |  | 48 | Floor (×28); Wall (×20) | 0 | 0 | 0 | 48
B09 | RF_POLIMI-LC_IH-E | Roof | Notebook (manual layers) | 36 | 4 |  | 0.1 | 0.04 |  |  | 52 | Roof (×50); Wall (×2) | 52 | 0 | 0 | 0
B10 | Generic Interior Wall | Internal partition | HB default (no BIM match) | 0 | 3 |  | 0.13 | 0.13 |  |  | 4 | Wall (×4) | 0 | 0 | 0 | 4
B10 | Generic Interior Floor | Internal floor | HB default (no BIM match) | 0 | 3 |  | 0.1 | 0.1 |  |  | 20 | Floor (×16); Wall (×4) | 0 | 0 | 0 | 20
B10 | WL_POLIMI-LC_EW01 | External wall | IFC IfcMaterialLayerSet | 3 | 8 |  | 0.13 | 0.04 |  |  | 3 | Wall (×3) | 3 | 0 | 0 | 0
B10 | WL_POLIMI-LC_EW02 | External wall | IFC IfcMaterialLayerSet | 4 | 8 |  | 0.13 | 0.04 |  |  | 33 | Wall (×33) | 26 | 0 | 7 | 0
B10 | WL_POLIMI-LC_EW03 | External wall | IFC IfcMaterialLayerSet | 8 | 9 |  | 0.13 | 0.04 |  |  | 8 | Wall (×8) | 8 | 0 | 0 | 0
B10 | WL_POLIMI-LC_FC300 | External wall | IFC IfcMaterialLayerSet | 31 | 3 |  | 0.13 | 0.04 |  |  | 37 | Wall (×37) | 15 | 0 | 0 | 22
B10 | WL_POLIMI-LC_EW04 | External wall | IFC IfcMaterialLayerSet | 1 | 7 |  | 0.13 | 0.04 |  |  | 1 | Wall (×1) | 1 | 0 | 0 | 0
B10 | WL_POLIMI-LC_EW05 | External wall | IFC IfcMaterialLayerSet | 2 | 9 |  | 0.13 | 0.04 |  |  | 2 | Wall (×2) | 2 | 0 | 0 | 0
B10 | WL_POLIMI-LC_IW02 | Internal partition | IFC IfcMaterialLayerSet | 58 | 7 |  | 0.13 | 0.13 |  |  | 78 | Wall (×78) | 20 | 0 | 0 | 58
B10 | WL_POLIMI-LC_IW03 | Internal partition | IFC IfcMaterialLayerSet | 24 | 3 |  | 0.13 | 0.13 |  |  | 34 | Wall (×34) | 14 | 0 | 0 | 20
B10 | WL_POLIMI-LC_IW04 | Internal partition | IFC IfcMaterialLayerSet | 22 | 8 |  | 0.13 | 0.13 |  |  | 42 | Wall (×42) | 2 | 0 | 0 | 40
B10 | WL_POLIMI-LC_IW06_Toilet | Internal partition | IFC IfcMaterialLayerSet | 4 | 5 |  | 0.13 | 0.13 |  |  | 4 | Wall (×4) | 4 | 0 | 0 | 0
B10 | WL_POLIMI-LC_IW01 | Internal partition | IFC IfcMaterialLayerSet | 7 | 6 |  | 0.13 | 0.13 |  |  | 11 | Wall (×11) | 3 | 0 | 0 | 8
B10 | WL_POLIMI-LC_IW05_Toilet | Internal partition | IFC IfcMaterialLayerSet | 7 | 9 |  | 0.13 | 0.13 |  |  | 7 | Wall (×7) | 7 | 0 | 0 | 0
B10 | FL_POLIMI-LC_InternalFloor_IH-E | Floor over outdoor/unheated | IFC IfcMaterialLayerSet | 3 | 5 |  | 0.17 | 0.04 |  |  | 79 | Floor (×48); Wall (×31) | 13 | 0 | 0 | 66
B10 | FL_POLIMI-LC_GroundFloor | Ground floor | IFC IfcMaterialLayerSet | 21 | 7 |  | 0.17 | 0 |  |  | 15 | Floor (×13); Wall (×2) | 0 | 15 | 0 | 0
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | Internal floor | IFC IfcMaterialLayerSet | 11 | 5 |  | 0.1 | 0.1 |  |  | 22 | Floor (×12); Wall (×10) | 0 | 0 | 0 | 22
B10 | RF_POLIMI-LC_IH-E | Roof | Notebook (manual layers) | 12 | 4 |  | 0.1 | 0.04 |  |  | 17 | Roof (×15); Wall (×2) | 17 | 0 | 0 | 0
Note on E1: Number of IfcWall/IfcSlab instances whose type name matches this construction.
Note on H1: Input (blue). Conventional ISO 6946 surface resistances by category; edit if needed. Ground floor: Rse = 0 (soil not included).
Note on J1: Formula: SUMIFS of Val_Layers R = d/λ for this building + construction (as modelled in the IDF, air cavities treated as massive layers).
Note on K1: Formula: 1 / (Rsi + R layers + Rse). Indicative steady-state U of the IDF construction; E+ uses its own dynamic film coefficients.

## Val_Layers
Building | Construction | Layer # (outside → inside) | Material (E+ name) | Material (IFC name) | Thickness (m) | Conductivity λ (W/m·K) | Density ρ (kg/m³) | Specific heat c (J/kg·K) | Thermal absorptance | Solar absorptance | Visible absorptance | Roughness | R = d/λ (m²K/W)
B09 | Generic Interior Wall | 1 | Generic Gypsum Board | Generic Gypsum Board | 0.0127 | 0.16 | 800 | 1090 | 0.9 | 0.5 | 0.5 | MediumSmooth
B09 | Generic Interior Wall | 2 | Generic Wall Air Gap | Generic Wall Air Gap | 0.1 | 0.667 | 1.28 | 1000 | 0.9 | 0.7 | 0.7 | Smooth
B09 | Generic Interior Wall | 3 | Generic Gypsum Board | Generic Gypsum Board | 0.0127 | 0.16 | 800 | 1090 | 0.9 | 0.5 | 0.5 | MediumSmooth
B09 | Generic Interior Floor | 1 | Generic Acoustic Tile | Generic Acoustic Tile | 0.02 | 0.06 | 368 | 590 | 0.9 | 0.2 | 0.2 | MediumSmooth
B09 | Generic Interior Floor | 2 | Generic Ceiling Air Gap | Generic Ceiling Air Gap | 0.1 | 0.556 | 1.28 | 1000 | 0.9 | 0.7 | 0.7 | Smooth
B09 | Generic Interior Floor | 3 | Generic LW Concrete | Generic LW Concrete | 0.1 | 0.53 | 1280 | 840 | 0.9 | 0.8 | 0.8 | MediumRough
B09 | Generic Ground Slab | 1 | Generic 50mm Insulation | Generic 50mm Insulation | 0.05 | 0.03 | 43 | 1210 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | Generic Ground Slab | 2 | Generic HW Concrete | Generic HW Concrete | 0.2 | 1.95 | 2240 | 900 | 0.9 | 0.8 | 0.8 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 6 | dtu_MT_POLIMI_CLS-0.425 | dtu_MT_POLIMI_CLS | 0.425 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW04 | 7 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 3 | dtu_MT_POLIMI_Isolante rigido-0.06 | dtu_MT_POLIMI_Isolante rigido | 0.06 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.2 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.2 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 6 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW01 | 8 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 6 | dtu_MT_POLIMI_CLS-0.425 | dtu_MT_POLIMI_CLS | 0.425 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 7 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 8 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW03 | 9 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 6 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.425 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.425 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 7 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 8 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW05 | 9 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.26 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.26 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 6 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_EW02 | 8 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-2 | 1 | dtu_MT__POLIMI_Intonaco interno-0.015 | dtu_MT__POLIMI_Intonaco interno | 0.015 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-2 | 2 | Calcestruzzo- gettato in opera-0.26 | Calcestruzzo- gettato in opera | 0.26 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-2 | 3 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-2 | 4 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-2 | 5 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 1 | dtu_MT__POLIMI_Intonaco interno-0.015 | dtu_MT__POLIMI_Intonaco interno | 0.015 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 3 | dtu_MT_POLIMI_Isolante morbido-0.1 | dtu_MT_POLIMI_Isolante morbido | 0.1 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 4 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.15 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.15 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 5 | Calcestruzzo- gettato in opera-0.26 | Calcestruzzo- gettato in opera | 0.26 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 6 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_FC300-3 | 8 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 3 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 4 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 5 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 6 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW02 | 7 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW03 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW03 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW03 | 3 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 3 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 4 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 5 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 6 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 7 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW04 | 8 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 1 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 2 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 3 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 4 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 5 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 6 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 8 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW05_Toilet | 9 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW06_Toilet | 1 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW06_Toilet | 2 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW06_Toilet | 3 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW06_Toilet | 4 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | WL_POLIMI-LC_IW06_Toilet | 5 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 1 | dtu_MT_POLIMI_Pavimento industriale-0.06 | dtu_MT_POLIMI_Pavimento industriale | 0.06 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 2 | dtu_MT_POLIMI_Massetto-0.08 | dtu_MT_POLIMI_Massetto | 0.08 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 3 | dtu_MT_POLIMI_Isolante rigido-0.06 | dtu_MT_POLIMI_Isolante rigido | 0.06 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 4 | dtu_MT_POLIMI_CLS-0.05 | dtu_MT_POLIMI_CLS | 0.05 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 5 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.35 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.35 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 6 | dtu_MT_POLIMI_Magrone-0.1 | dtu_MT_POLIMI_Magrone | 0.1 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_GroundFloor | 7 | dtu_MT_Ghiaia-0.2 | dtu_MT_Ghiaia | 0.2 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 1 | dtu_MT_POLIMI_Piastrelle-0.01 | dtu_MT_POLIMI_Piastrelle | 0.01 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 2 | dtu_MT_Massetto-0.15 | dtu_MT_Massetto | 0.15 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 4 | dtu_MT_Solaio laterocemento-0.15 | dtu_MT_Solaio laterocemento | 0.15 | 0.66 | 1100 | 839 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 5 | dtu_MT__POLIMI_Intonaco interno-0.02 | dtu_MT__POLIMI_Intonaco interno | 0.02 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B09 | RF_POLIMI-LC_IH-E | 1 | dtu_MT_POLIMI_Ghiaia-0.08 | dtu_MT_POLIMI_Ghiaia | 0.08 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | RF_POLIMI-LC_IH-E | 2 | dtu_MT_POLIMI_Massetto-0.12 | dtu_MT_POLIMI_Massetto | 0.12 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | RF_POLIMI-LC_IH-E | 3 | dtu_MT_POLIMI_Isolante rigido-0.08 | dtu_MT_POLIMI_Isolante rigido | 0.08 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B09 | RF_POLIMI-LC_IH-E | 4 | dtu_MT_POLIMI_CLS-0.25 | dtu_MT_POLIMI_CLS | 0.25 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | Generic Interior Wall | 1 | Generic Gypsum Board | Generic Gypsum Board | 0.0127 | 0.16 | 800 | 1090 | 0.9 | 0.5 | 0.5 | MediumSmooth
B10 | Generic Interior Wall | 2 | Generic Wall Air Gap | Generic Wall Air Gap | 0.1 | 0.667 | 1.28 | 1000 | 0.9 | 0.7 | 0.7 | Smooth
B10 | Generic Interior Wall | 3 | Generic Gypsum Board | Generic Gypsum Board | 0.0127 | 0.16 | 800 | 1090 | 0.9 | 0.5 | 0.5 | MediumSmooth
B10 | Generic Interior Floor | 1 | Generic Acoustic Tile | Generic Acoustic Tile | 0.02 | 0.06 | 368 | 590 | 0.9 | 0.2 | 0.2 | MediumSmooth
B10 | Generic Interior Floor | 2 | Generic Ceiling Air Gap | Generic Ceiling Air Gap | 0.1 | 0.556 | 1.28 | 1000 | 0.9 | 0.7 | 0.7 | Smooth
B10 | Generic Interior Floor | 3 | Generic LW Concrete | Generic LW Concrete | 0.1 | 0.53 | 1280 | 840 | 0.9 | 0.8 | 0.8 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 3 | dtu_MT_POLIMI_Isolante rigido-0.06 | dtu_MT_POLIMI_Isolante rigido | 0.06 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.2 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.2 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 6 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW01 | 8 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.26 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.26 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 6 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW02 | 8 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 6 | dtu_MT_POLIMI_CLS-0.425 | dtu_MT_POLIMI_CLS | 0.425 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 7 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 8 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW03 | 9 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_FC300 | 1 | dtu_MT__POLIMI_Intonaco interno-0.015 | dtu_MT__POLIMI_Intonaco interno | 0.015 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_FC300 | 2 | Calcestruzzo- gettato in opera-0.26 | Calcestruzzo- gettato in opera | 0.26 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_FC300 | 3 | dtu_MT__POLIMI_Intonaco interno-0.015 | dtu_MT__POLIMI_Intonaco interno | 0.015 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 6 | dtu_MT_POLIMI_CLS-0.425 | dtu_MT_POLIMI_CLS | 0.425 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW04 | 7 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 1 | dtu_MT_POLIMI_Pannello in alluminio-0.005 | dtu_MT_POLIMI_Pannello in alluminio | 0.005 | 220 | 2700 | 896 | 0.2 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 2 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.035 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.035 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 4 | dtu_MT_POLIMI_Membrana impermeabilizzante-0.005 | dtu_MT_POLIMI_Membrana impermeabilizzante | 0.005 | 0.23 | 1100 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 5 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata-0.265 | dtu_MT_POLIMI_Camera d'aria debolmente ventilata | 0.265 | 1 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 6 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.425 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.425 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 7 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 8 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_EW05 | 9 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 3 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 4 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 5 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 6 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW02 | 7 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW03 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW03 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW03 | 3 | dtu_MT_POLIMI_Isolante morbido-0.065 | dtu_MT_POLIMI_Isolante morbido | 0.065 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 1 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 3 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 4 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 5 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 6 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 7 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW04 | 8 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW06_Toilet | 1 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW06_Toilet | 2 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW06_Toilet | 3 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW06_Toilet | 4 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW06_Toilet | 5 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 1 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 2 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 3 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 4 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.04 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.04 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 5 | dtu_MT_Calcestruzzo armato-0.3 | dtu_MT_Calcestruzzo armato | 0.3 | 2.3 | 2399.96 | 1000 | 0.85 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW01 | 6 | dtu_MT__POLIMI_Intonaco interno-0.02 | dtu_MT__POLIMI_Intonaco interno | 0.02 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 1 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 2 | dtu_MT__POLIMI_Intonaco interno-0.01 | dtu_MT__POLIMI_Intonaco interno | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 3 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 4 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 5 | dtu_MT_POLIMI_Camera d'aria non ventilata-0.065 | dtu_MT_POLIMI_Camera d'aria non ventilata | 0.065 | 1 | 1 | 1003 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 6 | dtu_MT_POLIMI_Isolante morbido-0.04 | dtu_MT_POLIMI_Isolante morbido | 0.04 | 0.04 | 80 | 1028 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 7 | dtu_MT_POLIMI_Gypsum Board-0.025 | dtu_MT_POLIMI_Gypsum Board | 0.025 | 0.21 | 900 | 1000 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 8 | dtu_MT_POLIMI_Intonaco gesso puro-0.01 | dtu_MT_POLIMI_Intonaco gesso puro | 0.01 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | WL_POLIMI-LC_IW05_Toilet | 9 | dtu_MT_POLIMI_Piastrelle-0.015 | dtu_MT_POLIMI_Piastrelle | 0.015 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-E | 1 | dtu_MT_POLIMI_Linoleum-0.01 | dtu_MT_POLIMI_Linoleum | 0.01 | 0.041 | 50 | 2301 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-E | 2 | dtu_MT_Massetto-0.15 | dtu_MT_Massetto | 0.15 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-E | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-E | 4 | dtu_MT_Solaio laterocemento-0.15 | dtu_MT_Solaio laterocemento | 0.15 | 0.66 | 1100 | 839 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-E | 5 | dtu_MT__POLIMI_Intonaco interno-0.02 | dtu_MT__POLIMI_Intonaco interno | 0.02 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 1 | dtu_MT_POLIMI_Pavimento industriale-0.06 | dtu_MT_POLIMI_Pavimento industriale | 0.06 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 2 | dtu_MT_POLIMI_Massetto-0.08 | dtu_MT_POLIMI_Massetto | 0.08 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 3 | dtu_MT_POLIMI_Isolante rigido-0.06 | dtu_MT_POLIMI_Isolante rigido | 0.06 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 4 | dtu_MT_POLIMI_CLS-0.05 | dtu_MT_POLIMI_CLS | 0.05 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 5 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata-0.35 | dtu_MT_POLIMI_Camera d'aria fortemente ventilata | 0.35 | 0.285 | 1 | 1004 | 0.7 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 6 | dtu_MT_POLIMI_Magrone-0.1 | dtu_MT_POLIMI_Magrone | 0.1 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_GroundFloor | 7 | dtu_MT_Ghiaia-0.2 | dtu_MT_Ghiaia | 0.2 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 1 | dtu_MT_POLIMI_Piastrelle-0.01 | dtu_MT_POLIMI_Piastrelle | 0.01 | 1.3 | 2300 | 839 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 2 | dtu_MT_Massetto-0.15 | dtu_MT_Massetto | 0.15 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 3 | dtu_MT_POLIMI_Isolante rigido-0.1 | dtu_MT_POLIMI_Isolante rigido | 0.1 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 4 | dtu_MT_Solaio laterocemento-0.15 | dtu_MT_Solaio laterocemento | 0.15 | 0.66 | 1100 | 839 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | FL_POLIMI-LC_InternalFloor_IH-IH_Toilet | 5 | dtu_MT__POLIMI_Intonaco interno-0.02 | dtu_MT__POLIMI_Intonaco interno | 0.02 | 0.35 | 1200 | 999 | 0.9 | 0.7 | 0.7 | MediumRough
B10 | RF_POLIMI-LC_IH-E | 1 | dtu_MT_POLIMI_Ghiaia-0.08 | dtu_MT_POLIMI_Ghiaia | 0.08 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | RF_POLIMI-LC_IH-E | 2 | dtu_MT_POLIMI_Massetto-0.12 | dtu_MT_POLIMI_Massetto | 0.12 | 1.2 | 1700 | 1000 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | RF_POLIMI-LC_IH-E | 3 | dtu_MT_POLIMI_Isolante rigido-0.08 | dtu_MT_POLIMI_Isolante rigido | 0.08 | 0.04 | 30 | 1452 | 0.95 | 0.7 | 0.7 | MediumRough
B10 | RF_POLIMI-LC_IH-E | 4 | dtu_MT_POLIMI_CLS-0.25 | dtu_MT_POLIMI_CLS | 0.25 | 1.046 | 2300 | 657 | 0.95 | 0.7 | 0.7 | MediumRough

## Val_Glazing
Building | Construction (E+) | BIM source | Layer(s) | U-factor (W/m²K) | SHGC | VT | N fenestration surfaces | N with external blind
B09 | Generic Double Pane | HB default | Generic Low-e Glass / Generic Window Air Gap / Generic Clear Glass |  |  |  | 23 | 0
B09 | windowConstruction_U0.9_SHGC0.67_VT0.8 | IfcWindow / IfcDoor pset | windowConstruction_U0.9_SHGC0.67_VT0.8 Material | 0.9 | 0.67 | 0.8 | 1 | 0
B09 | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.8 | Curtain wall (IfcWall …CurtainWall pset) | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.8 Material | 0.9 | 0.67 | 0.8 | 31 | 11
B10 | windowConstruction_U0.9_SHGC0.67_VT0.8 | IfcWindow / IfcDoor pset | windowConstruction_U0.9_SHGC0.67_VT0.8 Material | 0.9 | 0.67 | 0.8 | 2 | 1
B10 | windowConstruction_U0.9_SHGC0.67_VT0.58 | IfcWindow / IfcDoor pset | windowConstruction_U0.9_SHGC0.67_VT0.58 Material | 0.9 | 0.67 | 0.58 | 2 | 0
B10 | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.8 | Curtain wall (IfcWall …CurtainWall pset) | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.8 Material | 0.9 | 0.67 | 0.8 | 12 | 1
B10 | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.58 | Curtain wall (IfcWall …CurtainWall pset) | curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.58 Material | 0.9 | 0.67 | 0.58 | 9 | 2
Note on C1: 'HB default' = Generic Double Pane (Low-e 6 mm / air 12.7 mm / clear 6 mm) kept when no BIM glazing data matched the aperture (B09: 23 curtain-wall panels whose TBIM VT 0.58 has no matching construction).

## Val_Schedules
Family | Source | Schedule id (E+ Name) | N day schedules | N rules | Max value | E+ object | ScheduleTypeLimits | B09: references in IDF | B10: references in IDF | Change in calibrated IDF (Field_1 …)
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_A0.1/A0.2 | 18 | 18 | 0.33 | Schedule:Compact | occupancyScheduleTypeLimit | 0 | 2
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_A1.1 | 18 | 18 | 1 | Schedule:Compact | occupancyScheduleTypeLimit | 0 | 1
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_A1.2 | 18 | 18 | 0.59 | Schedule:Compact | occupancyScheduleTypeLimit | 0 | 1
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_A1.3 | 18 | 18 | 0.47 | Schedule:Compact | occupancyScheduleTypeLimit | 0 | 1
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.1 | 18 | 18 | 1.07 | Schedule:Compact | occupancyScheduleTypeLimit | 2 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.2 | 18 | 18 | 0.47 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.3 | 18 | 18 | 0.39 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.4 | 18 | 18 | 0.78 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.5 | 18 | 18 | 0.31 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.6 | 18 | 18 | 0.44 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B0.7 | 18 | 18 | 0.77 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B1.1 | 18 | 18 | 0.75 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B1.2 | 18 | 18 | 0.64 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B1.3 | 18 | 18 | 0.86 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B1.4 | 18 | 18 | 0.76 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B1.5 | 18 | 18 | 0.37 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.1 | 18 | 18 | 0.93 | Schedule:Compact | occupancyScheduleTypeLimit | 0 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.2 | 18 | 18 | 0.57 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.3 | 18 | 18 | 0.66 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.4 | 18 | 18 | 0.15 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.5 | 18 | 18 | 0.66 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_B2.6 | 18 | 18 | 0.35 | Schedule:Compact | occupancyScheduleTypeLimit | 1 | 0
Occupancy | Schedules_Occupancy_PoliMi_LC.json | OccSch_Unoccupied | 1 | 1 | 0 | Schedule:Compact | occupancyScheduleTypeLimit | 47 | 15
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_A0.1/A0.2 | 18 | 18 | 0.33 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 1
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_A1.1 | 18 | 18 | 1 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 1
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_A1.2 | 18 | 18 | 0.59 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 1
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_A1.3 | 18 | 18 | 0.47 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 1
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.1 | 18 | 18 | 1.07 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.2 | 18 | 18 | 0.47 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.3 | 18 | 18 | 0.39 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.4 | 18 | 18 | 0.78 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.5 | 18 | 18 | 0.31 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.6 | 18 | 18 | 0.44 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B0.7 | 18 | 18 | 0.77 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B1.1 | 18 | 18 | 0.75 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B1.2 | 18 | 18 | 0.64 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B1.3 | 18 | 18 | 0.86 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B1.4 | 18 | 18 | 0.76 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B1.5 | 18 | 18 | 0.37 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.1 | 18 | 18 | 0.93 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.2 | 18 | 18 | 0.57 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.3 | 18 | 18 | 0.66 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.4 | 18 | 18 | 0.15 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.5 | 18 | 18 | 0.66 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_B2.6 | 18 | 18 | 0.35 | Schedule:Compact | equipmentScheduleTypeLimit | 0 | 0
Equipment | Schedules_Equipment_PoliMi_LC.json | EqpSch_Unoccupied | 1 | 1 | 0.05 | Schedule:Compact | equipmentScheduleTypeLimit | 1 | 5
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_A0.1/A0.2 | 18 | 18 | 0.33 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 1
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_A1.1 | 18 | 18 | 1 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 1
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_A1.2 | 18 | 18 | 0.59 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 1
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_A1.3 | 18 | 18 | 0.47 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 1
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.1 | 18 | 18 | 1.07 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.2 | 18 | 18 | 0.47 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.3 | 18 | 18 | 0.39 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.4 | 18 | 18 | 0.78 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.5 | 18 | 18 | 0.31 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.6 | 18 | 18 | 0.44 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B0.7 | 18 | 18 | 0.77 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B1.1 | 18 | 18 | 0.75 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B1.2 | 18 | 18 | 0.64 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B1.3 | 18 | 18 | 0.86 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B1.4 | 18 | 18 | 0.76 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B1.5 | 18 | 18 | 0.37 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.1 | 18 | 18 | 0.93 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.2 | 18 | 18 | 0.57 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.3 | 18 | 18 | 0.66 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.4 | 18 | 18 | 0.15 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.5 | 18 | 18 | 0.66 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_B2.6 | 18 | 18 | 0.35 | Schedule:Compact | lightingScheduleTypeLimit | 0 | 0
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_Unoccupied | 1 | 1 | 1 | Schedule:Compact | lightingScheduleTypeLimit | 1 | 4
Lighting | Schedules_Lighting_PoliMi_LC.json | LghSch_Costant | 1 | 1 | 1 | Schedule:Compact | lightingScheduleTypeLimit | 55 | 7 | B09: Through: 12/31 , For: AllDays , Until: 07:00 , 0 , Until: 18:00 , 1 , Until: 24:00 , 0 ¦ B10: Through: 12/31 , For: AllDays , Until: 07:00 , 0 , Until: 18:00 , 1 , Until: 24:00 , 0
Heating | Schedules_Heating_PoliMi_LC.json | HtnSch_AHU | 1 | 2 | 1 | Schedule:Compact | availabilityScheduleTypeLimit | 52 | 12 | B09: Through: 4/15 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 , Through: 12/31 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 ¦ B10: Through: 4/15 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 , Through: 12/31 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1
Cooling | Schedules_Cooling_PoliMi_LC.json | ClnSch_AHU | 2 | 3 | 1 | Schedule:Compact | availabilityScheduleTypeLimit | 52 | 12 | B09: Through: 4/16 , For: AllDays , Until: 24:00 , 1 , Through: 10/14 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 , Through: 12/31 , For: AllDays , Until: 24:00 , 1 ¦ B10: Through: 4/16 , For: AllDays , Until: 24:00 , 1 , Through: 10/14 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 , Through: 12/31 , For: AllDays , Until: 24:00 , 1
Ventilation | Schedules_Ventilation_PoliMi_LC.json | VntSch_AHU | 1 | 1 | 1 | Schedule:Compact | availabilityScheduleTypeLimit | 52 | 12 | B09: Through: 12/31 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1 ¦ B10: Through: 12/31 , For: AllDays , Until: 7:00 , 1 , Until: 18:00 , 1 , Until: 24:00 , 1
Equipment | created in notebook | EqpSch_Costant | – | – | 0 | Schedule:Compact | equipmentScheduleTypeLimit | 55 | 6 | B09: Through: 12/31 , For: AllDays , Until: 07:00 , 0 , Until: 18:00 , 1 , Until: 24:00 , 0
Availability | created in notebook | AlwaysOff | – | – | 0 | Schedule:Compact | availabilityScheduleTypeLimit | 57 | 34
Note on C1: Lecture-hall schedules A* belong to Building 10, B* to Building 09; both sets are written to both IDFs.
Note on I1: Number of People / Lights / ElectricEquipment / IdealLoads availability fields that point to this schedule (baseline IDF).

## Issues_Questions
ID | Severity | Topic | What the manuscript says | What the code / models do | Evidence | Suggested action | Question for the authors | Resolution / author decision
I01 | High | Table 7 values | Assigned values such as 8.0 W/m² LPD, 5.0/8.0 W/m² EPD, 0.80 pp/m² classrooms, 0.10 pp/m² offices, 120 persons 'Room A1.3', 2.5 h⁻¹, 60/40 % RH, 26/24/20/15 °C, 'Eurocode 1 / Class 3'. | TBIM/IDF: LPD 6 W/m² (7 office); EPD undefined → 0 (baseline), 2/10 W/m² (calibrated); 0.6 pp/m² lecture halls, 0.3 labs, 0.12 office, 0.8 snack bar; RH 70/40 %; temperatures 26/23/23.5/18 °C (not used); wind class A4. | Val_SpaceTypes, Val_Zones | Replace the 'Assigned value' column with Val_SpaceTypes (per occupancy type) and mark which values reach the IDF (Map_Spaces 'In IDF?'). | Where do the current Table 7 values come from (another building, a draft, a standard)? May I replace them with the model values? | Author: replace with model values from the CALIBRATED IDF, reported by E+ zone → see T7_Zones / T7_Grouped.
I02 | High | Table 8 values | Construction names ExtWall_PrefabConcrete_12cmIns / Roof_InsulatedSlab / Floor_GroundSlab; U = 0.28 / 0.22 / 0.30 / 0.95 W/m²K. | Model constructions are WL_POLIMI-LC_EW01–05, FC300-*, IW01–06, FL_POLIMI-LC_*, RF_POLIMI-LC_IH-E with multilayer IFC material sets; U-values are not read from IFC but computed by E+ from layers. | Val_Constructions (U computed), Val_Layers | Rebuild Table 8 as one row per construction: name, category, layers (d, λ, ρ, c), computed U. | Do you want Table 8 per construction (long) or only the envelope types actually exposed to outdoors (EW*, FC*, RF, FL ground)? | Author: list every outer-envelope construction → see T8_Envelope.
I03 | High | Table 9 values | U 1.40, glass U 1.10, SHGC 0.45, VT 0.65, glazing fraction 0.85, 2.80 × 1.50 m, anodised Al with thermal break. | IFC/IDF: U 0.9, SHGC 0.67, VT 0.8 (and 0.58 in B10), glass U 1.1, frame U 0.7, aluminium, glazing fraction 0.8 (not used), double glazing; E+ simple glazing model. | Map_Apertures, Val_Glazing | Replace values; state that only U/SHGC/VT are used (WindowMaterial:SimpleGlazingSystem). |  | Replaced with model values → see T9_Glazing.
I04 | High | Temperature setpoints | Methods: 'Thermal and humidity control data … including temperature and humidity setpoints' are assigned from IFC to IdealLoads. | Only humidity setpoints are transferred. Thermostat = HB constant 20/26 °C (baseline); calibrated IDFs use hand-edited schedules (B09 15/18 °C heating, 20 °C cooling; B10 18/22 °C heating, 22 °C cooling). TBIM 18–23.5 / 23–26 °C limits are aggregated but never written. | Operation.py:541 HBRoomSetSetpointSchedules; IDF HVACTemplate:Thermostat | Either implement the mapping (pr_SpaceTemperatureWinterMin → heating SP, pr_SpaceTemperatureSummerMax → cooling SP) or correct the text. | Which setpoints should the paper report: TBIM design values or calibrated operating values? | Author: keep the setpoints cited in the paper → T7 reports 20 °C occupied / 15 °C setback heating and 26 °C cooling (Ref_Assumptions C8:C10); calibrated-IDF setpoints kept in T7_Zones columns Y–Z for traceability.
I05 | Medium | Equipment power density | Table 7 gives 5.0/8.0 W/m². | pr_EquipmentPowerDensity = 'Undefined' in every TBIM cell → 0 W/m² in the baseline; calibrated values 2 W/m² (most zones) and 10 W/m² (B10 lecture halls) were typed directly in the IDF. | Val_SpaceTypes, Val_Zones | Document the calibrated values as calibration parameters, not BIM inputs. |  | Calibrated EPD (2 / 10 W/m²) reported in T7.
I06 | Medium | 'Costant' schedules | – | LghSch_Costant and EqpSch_Costant are 0 all year in the baseline IDF, so lights/equipment in zones using them never switch on; calibration changed them to 1 between 07:00 and 18:00. | Val_Schedules (column K) | Mention in calibration section.
I07 | High | Mechanical ventilation rate units | Table 7: 'given in air changes per hour, h⁻¹'. | Code writes pr_MechanicalVentilationRate / 1000 into Outdoor_Air_Flow_per_Zone_Floor_Area (m³/s·m²), i.e. treats it as L/s·m². Restrooms 8 → 0.008 m³/s·m² (28.8 m³/h·m²). | Map_Spaces S15; scripts/01_bim_to_bem.py ('Mechanical ventilation rate') | Fix unit (ACH → DSOA 'Outdoor_Air_Flow_Air_Changes_per_Hour') or relabel the TBIM property. | Is pr_MechanicalVentilationRate in h⁻¹ or in L/s·m²? | Resolved by comparison with standard rates: pr_MechanicalVentilationRate is an air-change rate (h⁻¹) = N_peak × 7 L/s·p × 3.6 / V_net (e.g. 88 × 25.2 / 421.26 = 5.264 h⁻¹ stored as 5.26421); restrooms 8 h⁻¹ and stairs 1 h⁻¹ are UNI 10339-type extraction rates. The workflow error (h⁻¹ read as L/s·m²) scales by room height / 3.6 m (≈ 1.1 for 3.9–4 m rooms). Superseded in T7 by the EN 16798 values.
I08 | Medium | Zone aggregation bug | Methods: 'aggregation functions are applied to transfer energy-related parameters from cells to zones'. | Utils.TopologicZoneInheritSpaceData computes prevalent schedules (rl_ZoneIsScheduledBy_*) and a volume-weighted ventilation rate, but stores the LAST cell's rl_IsScheduledBy_* and pr_MechanicalVentilationRate instead (Operation.py:170–175). | Operation.py:169–176 | Use pr_ZoneMechanicalVentilationRate and rl_ZoneIsScheduledBy_* in zoneDictValues.
I09 | Medium | Infiltration | Table 7 / methods: 0.30 h⁻¹ baseline infiltration; 'pure infiltration at 0.3 ACH' at night. | ZoneInfiltration:DesignFlowRate, Flow/ExteriorArea = 0.0001 m³/s·m² ('TightBuilding'), schedule 'Generic Office Infiltration' from the HB office program. | Map_Model M09 | Align text or model. | Which value was used for the results in the paper? | Author: EN 16798 / Methods values are the reference → T7 reports 0.30 h⁻¹ (Ref_Assumptions); the repository IDF value is kept for traceability.
I10 | High | Outdoor air | 10 L/s·person + 0.6 L/s·m², EN 16798-1 Cat. II, AHU caps 11 000 / 7 200 m³/h, zero OA at night. | 7 L/s·person (0.007 m³/s), per-area = TBIM rate/1000, method 'Maximum' (not sum), ventilation availability VntSch_AHU 07–18 h (baseline) / always on (calibrated), ideal-loads capacity autosized (no caps). | Map_Spaces S15–S16, S31; Map_Model M07 | Align text or model. | Were the EN 16798 values applied in a later model version not in models/? | Author: keep the values already reported in the paper (10 L/s·p, 0.6 L/s·m², EN 16798-1 Cat. II as stated, 0 OA when unoccupied, AHU caps) → Ref_Assumptions.
I11 | Medium | Doors | Methods: IfcDoorType → HB Door objects. | Doors are converted into glazed HB Apertures with a window construction; HB/E+ Door objects are never created, and only 1 door (B09) / 3 doors (B10) reach the IDF because apertures on curtain-wall or adiabatic faces are discarded. In B09, 23 curtain-wall apertures keep HB 'Generic Double Pane': their TBIM VT is 0.58 but the B09 IFC only defines VT 0.8, so the construction 'curtainWallWindowConstruction_U0.9_SHGC0.67_VT0.58' is never created. Glazing data are read from instance psets, not types. | Map_Apertures A01, Val_Glazing | Correct text or map opaque doors to HB Door + OpaqueConstruction. | Should the 23 B09 curtain-wall panels use the VT 0.58 construction (as in the TBIM) instead of the HB default? | Author: in Table 9 only, the 23 B09 curtain-wall panels are reported with their BIM glazing (U 0.9, SHGC 0.67, VT 0.58); the IDF still uses HB Generic Double Pane.
I12 | Low | Roof construction | – | IfcRoofType carries no material layers; RF_POLIMI-LC_IH-E is typed in the notebook and also used for faces typed RF_POLIMI-LC_INH-E (B09). | Map_Envelope E14 | State this in the text.
I13 | Low | HB defaults with US conventions | – | Holidays 1/1 and 4/7, DST 12/3–5/11, office program (SHW 0.1 L/h·m², seated activity) come from HB defaults. | Map_Model M06, M10, M16 | Set Italian holidays/DST or mention.
I14 | Low | Timestep / run period | – | Baseline IDF timestep 6 (the nb line meant to set 4 is ineffective); calibrated IDF 4. Run period forced to 1/1–31/12/2024 at run time, while the paper's monitoring period is 1/2/2024–31/1/2025. | Map_Model M14–M15 | Report the run period used for calibration. | Which EPW was used for calibration: Lecco_IT-hour.epw (in repo) or the on-site station file described in the paper?
I15 | Low | Exposed interior partitions | – | Cells excluded from the BEM (notUsefullCellUIDs) leave their neighbours' partitions as 'Outdoors' surfaces (e.g. B09: 135 IW03, 21 IW06 faces). | Val_Constructions (Outdoors column) | Mention as a modelling simplification or set them adiabatic.
I16 | Low | Air cavities | – | Ventilated/unventilated cavities are written as massive Material layers (λ 0.285–1.0 W/m·K, ρ 1 kg/m³) instead of Material:AirGap or outer-layer removal. | Val_Layers | Mention or switch to Material:AirGap.
I17 | Low | B09 zoned TBIM | – | DigitMan_Model_POLIMI-Edificio09_Topologic-withZones.json does not match the B09 IDF zones (IDF has zone12-0/1/2, zone50, debugZone0–11 not present in the JSON), so a cell → zone table cannot be rebuilt reliably for B09. | models/ | Re-export the zoned TBIM from the run that produced the IDF. | Do you want a cell → zone membership table added (B10 only, or after re-running B09)? | Author: use E+ zones as reference → T7_Zones is indexed by E+ Zone name; no cell → zone table.
I18 | Medium | Fallback constructions | – | Faces whose type has no thermal layers (WL_VirtualWall, the opaque ≈19 % of curtain-wall faces, FL_VirtualFloor) keep HB defaults; 'Generic Exterior Wall' is then replaced by WL_POLIMI-LC_EW02 (B09: 156 surfaces vs 9 IFC walls of that type) and 'Generic Interior Wall/Floor' stay as HB generic layers (B09: 94 + 360 surfaces). | Val_Constructions (columns E vs L) | Mention in the text; consider an explicit construction for virtual and curtain-wall spandrel faces.
I19 | High | Outdoor air vs AHU capacity | Methods: 10 L/s·p + 0.6 L/s·m², bounded by AHU capacity 7 200 m³/h (B09) and 11 000 m³/h (B10). | With the E+ zone areas and People densities of the calibrated IDFs, design outdoor air (sum of per-person and per-area terms, all ventilated zones at full occupancy) is ≈ 94 500 m³/h for B09 (≈ 13 × AHU capacity) and ≈ 46 100 m³/h for B10 (≈ 4 ×). The AHU cap therefore governs at peak, giving ≈ 0.8 (B09) and ≈ 2.4 (B10) L/s·person effective. | Ref_Assumptions C12:C15 (live); T7_Zones column U | State that the cap binds at peak occupancy, or report the real occupancy / diversity used. | Is the AHU capacity applied to the sum of all zones (one AHU per building) and are design densities (0.6 pp/m² in lecture halls) the intended peak? | Author: keep the values already reported in the paper (no change). AHU check kept in Ref_Assumptions C12:C15 for information.
I20 | Medium | Calibrated setpoints | – | Calibrated IDFs: heating and cooling availability always on; B09 heating 18 °C (07–18 h) / 15 °C, cooling 20 °C all day; B10 heating 22 °C (07–18 h) / 18 °C, cooling 22 °C all day → zero dead-band in occupied hours, so ideal loads may heat and cool in the same day. | T7_Zones columns L–N; Val_Schedules | Confirm these are the intended calibrated setpoints before publishing them in Table 7. | Are the calibrated cooling setpoints (20 °C B09, 22 °C B10) intentional? | Author: Table 7 reports the setpoints cited in the paper; the calibrated IDF values are not reported in the Appendix.